ENGDOC#

GENERAL CABLE PLANT NOTES

SLAC

ELECTRICAL SYSTEMS DEPARTMENT

ID-236-801-36-RX2

Release Dated: 25-JAN-87

Last Revision  08/24/2016

SLAC NATIONAL ACCELERATOR LABORATORY

Operated by Stanford University for the U.S. Dept of Energy

Stanford University

Stanford, California

Proprietary data of Stanford University and/or U.S. Department of

Energy. Recipient shall not publish the information within unless

granted specific permission of Stanford University.

GENERAL CABLE PLANT NOTES

ELECTRICAL SYSTEMS DEPARTMENT

ID-236-801-36-RX2

Release Dated: 25-JAN-87

Last Revision 08/24/2016

## Introduction

This document explains, and is to be used in conjunction with, a CABLE INSTALLATION SCHEDULE.

The CABLE INSTALLATION SCHEDULE is supplied as another document in the total package of which this document is a part.

Note that this is a general document, and may contain much more information than may be required for the CABLE INSTALLATION SCHEDULE supplied. This is particularly true of the color code, cable types and cable termination tables which follow.

This document is divided into the following sections:

- Introduction

- General Notes

- Description of the CABLE INSTALLATION SCHEDULE

- Table 1 - Color Code Tables (and connection points) for Multi-Conductor Cables

- Table 2 - Cable Types and Cable Descriptions

- Table 3 - Cable Termination Descriptions

- Table 4 - Trim Codes for Coaxial Cable Terminations

- Table 5 - Document Revision Notes (for this document)

## General Notes

1. Some definitions and descriptions may not be fully defined at the time that this listing was printed. Any such known areas will be noted by a sequence of 2 or more X's (i.e. 'termination type LFB-XX' or 'tooling XX-XXX'). Any such missing information will be completed as later listings are printed. Additional (and missing) information will also be included in later revisions, as that information is given to the keeper of this document.

Note: where information is missing, PLEASE ASK QUESTIONS. Where such information is added, it will be so specifically listed in the revision notes section (last pages) of all subsequent listings.

2. Block diagrams and other informational drawings have been supplied as a part of the total package. Those drawings are also to be used as references to aid in the understanding of the CABLE INSTALLATION SCHEDULE, and this document.

3. A large number of short and medium length cables will be furnished already cut and terminated, ready for final connection by the subcontractor.

4. All long-haul cables are to be cut and generally terminated by the subcontractor. For details refer to the specific cable-end assembly instructions, and the other drawings and documents supplied with the total package.

5. The cable installation schedules list the exact location (+/- 2 feet, sufficient to resolve any ambiguities) of the components to which each end of any given cable is to be connected. Station marks will be stenciled on the wall at 50 feet intervals in collider housings, and may be indicated by drawings for off-line components. Additional information on these station locations is given in the section entitled 'Cable Installation Schedule Format Description' below.

The subcontractor shall refer to these station marks as may be required in order to locate all components.

6. GENERAL TERMINATION NOTE: FOR MULTIPLE POINT TERMINAL BLOCKS;

Terminal blocks are normally 50 point blocks. Each termination point has four flags -- A, B, C and D. Unless otherwise specifically noted, connect the indicated wire to flag 'C'.

The Cable Installation Schedule indicates the terminal block point numbers to be connected. The point numbers are called out at the right end of the 'ORIGIN' or 'DESTINATION' information field. For instance, -01/50, -26B50, -08C, etc., means to connect to points 1 through 50, the 'B' flag of points 26 through 50, and the 'C' flag of point 8, respectively. The points are wired in increasing numerical sequence, always starting with the first wire of the cable, per the indicated color code, to the lowest indicated number point. For the example given for 26B50, the first wire goes to point 26B, the second wire to point 27B, etc. If commas separate the numbers (for instance, -41,45B,43), rather than a slash, that means the first wire goes to point 41C, the second to point 45B and the third to point 43C.

The last two conductors of 52 conductor cables are generally not terminated. Also, some other cables are only partially wired. In all cases fold back and tape any unused conductors.

7. Termination Tooling.

It is IMPERATIVE that the correct tooling be used for:

a. trimming coaxial and other special cable for termination, and

b. for crimping, or other assembly, of any termination to any wire or coax.

Much of the required tooling is specified further on in this specification. Should any required tooling not be specified, or if it is desired to use any tooling other than that explicitly specified, such tooling REQUIRES THE PRIOR APPROVAL OF THE DESIGNATED SLAC INSPECTOR.

Any use of unspecified or non-approved tooling MAY REQUIRE THE REWORK OR REPLACEMENT OF THOSE CABLES AND/OR TERMINATIONS.

8. Cables not rated as tray cables or as Halogen Free Low Smoke must have the approval of the Electrical Safety Officer (ESO) or the Electrical Safety Committee (ESC) prior to requests for installation. Requests for installation should specify any additional steps required; I.E additional support or fire blocking.

## Cable Installation Schedule Format Description

The following is a description of the CABLE INSTALLATION SCHEDULE format:

FORMAL DEVICE NAME: This is the SLAC/SLC formal name for the system of which the indicated cable is a component. It is listed herein in order to allow quick reference to the actual control, readout, or other system as questions may occur. Example: QUAD:PI00,5920.

CABLE FUNCTION: This column gives a brief description of the function of the cable.

CABLE TYPE: This column gives the standard designation or an abbreviated form of it. Refer to TABLE 2 for the full and detailed description of any given cable.

CABLE NUMBER This column lists the cable identification number, a number that is unique to a single cable installed at SLAC. This number must be affixed to each end of each cable. Pre-assembled cables will normally be provided with the correct cable numbers attached. Other labels will be provided to the subcontractor for attachment at the time of cable installation.

ORIGIN / LOCATION: This column refers to the location of the cable's origin. The distinction between 'ORIGIN' and 'DESTINATION' is of particular importance when installing pre-assembled cables, in that any excess cable, over that needed for a service loop at the 'ORIGIN' end, is to be stored/distributed at the 'DESTINATION' end of the installed cable. Most cables originate at one of the instrument racks in a support building or collider housing alcove. For instance;

B136-1714-J10/J13 is to be interpreted as follows:

B136 indicates Building 136 17 indicates rack 17, chassis elevation 14(location in the rack) J10/J13 indicates JACK NOS. 10 through 13 on the chassis.

Occasionally, after the chassis elevation and jack (terminal board, etc.), additional digits will appear. They will be explained in TABLE 3 under the cable termination description, or a separate wire list will be furnished.

Similarly AS15-04-0132-TB1-1B25 is to be interpreted as follows;

AS15 indicates Arc South, in the area of Achromat 15 (which spans about 170 feet) 04 indicates Alcove 4 (in the South Arc), 0132 indicates rack 01, elevation 32, (rack 01 is the first (leftmost facing the rack fronts) rack. TB1 indicates TERMINAL BLOCK NO. 1 1B25 indicates POINTS 1 through 25. The 'B' indicates that this is a FASTON terminal block, and means wire to the 'B' flags only, and in the same sequence as the color code for that wire type. See the tables in Section 3 for the color codes.

Note that the first characters of this field (to the first '-') will take a form similar to one of the following:

- B(nnn), indicating a Building number

- KAnn, indicating an Alcove in the Klystron Gallery area, where (nn) is the sector number

- KFnn, indicating a Fiat in the Klystron Gallery area, where (nn) is the sector number

- KGnn, indicating a Klystron Gallery area, where (nn) is the sector number

- KMnn, indicating a Mechanical Alcove in the Klystron Gallery area, where (nn) is the sector number

- LInn, indicating a LInac housing area, again where (nn) is the sector number

- DKG, indicating a Damping ring device in sector 01 of the Klystron Gallery

- N or S, followed by DRV, DR, RTL or LTR. This indicates a North or South Damping ring area, as follows:

DRV indicates that the location is on the wall or floor of the Damping Ring Vault, but NOT on a ring girder. 
DR indicates a location actually on a Damping Ring girder 
LTR is in the Linac-To-Ring (east) housing, and 
RTL is in the Ring-To-Linac (west) housing.

Where LTR or RTL is followed by an S(n), the 'S' means that the location is on the wall or floor within that Section of the indicated housing.

Where LTR or RTL is followed by an (nn), the location is actually on a girder in the indicated housing, and the (nn) is the girder number.

- BSY indicates a location in the BEAM-SWITCHYARD (BSY) area.

- AN(nn) or AS(nn), indicating a location in the main Collider Arcs (North or South), the (nn) is the number of the Magnet Achromat (about 170 foot in length) spanning and/or including the exact location.
If (nn) is '00', the location is prior to the first Achromat, in the launch portion of the indicated Arc, but actually inside the BSY housing area.

If (nn) is '24' or '25', the locations are in the Final Focus area of the indicated tunnel. (The last 32 feet of '25' on each side are actually in the Collider Pit.)

- Additional information on the details for this field may be found in 'Data Entry Definitions for the SLC Cable Plant Program' (SLAC ELDDOC #83).

STATION: The exact location of a Beam Line related item is identified on the CABLE INSTALLATION SCHEDULE as a station number shown in feet, plus or minus 2 feet.

DESTINATION / LOCATION: This column is similar to 'ORIGIN' above, although many cables may find their destinations at a connection box or machine component on the actual Beam Line. Connection boxes and machine components are generally identified by the geographic area together with an abbreviated generic name. These components generally will be labeled, when they are in place at the time of the cable installation. Identification labels will probably not be found for devices not installed, and the LOCATION stations will be required to locate the given (future) connection point.

INSTALLATION NOTES: (Two entries, one each for ORIGIN and DESTINATION.)

1. The first field (left character in the field) is a code which indicates when, and by whom, the indicated end of a cable is terminated and connected. Each end of a cable is given an assembly code, and each end may require entirely different treatment.

This code is specifically decoded for the subcontractor on the second line of this field (see 'c.' below). The codes used are as follows:

- '0': No action to be taken by the subcontractor. This cable either exists, or is to be installed at a later time. It is listed for completeness of the CABLE INSTALLATION SCHEDULE, and especially to show the full sequence of a set of cables.

- '1': A cable with a pre-terminated end (an assembly) is delivered to the subcontractor. The subcontractor is to install the cable. The device connection is to be done later by others.

- '2': This cable has been previously installed, the subcontractor is only to terminate as indicated. Connection will be done later, by others.

- '3': The subcontractor is to install and terminate only. Connection is to be done later, by others.

- '4': The subcontractor is to make the indicated connections, the cable has been previously installed and terminated.

- '5': A cable with a pre-terminated end (an assembly) is delivered to the subcontractor. The subcontractor is to connect this end to the indicated device following cable installation.

- '6': The subcontractor is to terminate and connect only. The cable has been previously installed.

- '7': The subcontractor is to install, terminate and connect this end.

- '8': This end of the cable is terminated and partially installed. The subcontractor shall finish the cable installation and connect this end to the indicated device.

- '9': The cable is partially installed. The subcontractor shall finish the cable installation, terminate, and connect this end to the indicated device.

- '10': The cable is partially installed. The subcontractor shall finish the cable installation to the indicated device. Others will do the termination and connection later.

- '11': The cable is partially installed. The subcontractor shall finish the cable installation, and termination. Others will do the connection later.

- 'M': Commercially prefabricated (not built by SLAC or to a SLAC specification) I.E. a 6' AC power cord with molded ends.

- 'P': Commercially prefabricated (not built by SLAC or to a SLAC specification) I.E. a ribbon cable with non-molded connectors.

- 'S': Special termination and connection, to be done later, by others. The subcontractor is to only install the cable.

- 'SS': Termination and connection to be done later by others. The subcontractor to only install the cable. Any excess length at this end of the cable shall be neatly coiled as indicated in the subcontract's drawings and specifications.

TERMINATION:

a. This field is the code for the connector or termination hardware to be used. This information is always given, even if not directly needed by the subcontractor. See TABLE 3 for cable termination details and refer to TABLE 2 for a cable description and to TABLE1 in Section 3, as necessary, for the color code for that cable.

b. The second line of this field contains the code letters instructing the subcontractor on exactly what is to be done. If the second line is blank (see code '0' above), no action is to be taken by the subcontractor. Otherwise, any single code, or multiple combination of the codes, may occur.

LENGTH: This column gives the estimated cable length in feet. The exact length may be verified in the field. For some special cables, the indicated length is the delay time of the cable, in nanoseconds. Timing is indicated as a decimal number, ie. Length = '176' is 176 feet, Length = '176.0' is a delay time of 176.0 nanoseconds.

ROUTING SEQUENCE: This column refers to the routing of the cable in the raceway system. Refer to the tray layout drawings and key plans for details.

REV #: This column indicates the change level for the indicated cable ONLY. Blank indicates no change since original entry, '1' indicates one change, etc.

### Table 1 - Color Code Tables

(and connection points) for Multi-Conductor Cables.

The following tables are necessary or useful to complete the cable and connector descriptions given in this document.

TABLE 1 - ABBREVIATIONS USED FOR COLORS.

COLOR		2-PLACE		3-PLACE

CLEAR		CL		CLR

BLACK		BK		BLK

BROWN		BN		BRN

RED			RD		RED

ORANGE		OR		ORN

YELLOW		YE		YEL

GREEN		GN		GRN

BLUE		BU		BLU

VIOLET		VI		VIO

GREY		GY		GRY

WHITE		WT		WHT

PINK		PK		PNK

TAN			TN		TAN

3-place color designations are normally used, 2-place are listed for clarity in case they are used in any additional information.

The following is common information, which is used in the wire tables which follow:

a. * -- a pin designation letter preceded by a '*' (i.e. '*C') indicates that this letter is lower case letter (pin) on the connector.

b. ** -- where more than one color is given for a wire (i.e. ' WHT/RED/BLK') the first color is the base color of the insulation, The additional colors are the tracer (striping) colors.

### TABLE 1 - COLOR CODE 1A (NEMA PUB. NO. WC 30, TABLE 5-2)

The following standard color sequence can be applied to unpaired and paired cables.  An A and B

designation for the two wires in a pair is sometimes useful.  A “CABLE TERM. LETTER” is

given for convenience for use with multi-pin connectors that are wired to follow this standard color code

sequence.

Used With CABLE TYPES

4C8/3V	8C16/3V

12C12/3V	12C16/3V

12C22/3V	19C16/3V

26C16/3V	26C22/3V

52C16/3V	4C16T6V

8C16T6V	12C16T6V

26PR22OS	12C18/3V

2C12OS

UNPAIRED   **WIRE          PAIRED   CABLE     UNPAIRED   ** WIRE COLOR     PAIRED       CABLE

CABLE      COLOR           CABLE    TERM.     CABLE      CODE              CABLE PAIR   TERM.

COND NO.   CODE            PAIR     LETTER    COND. NO.                    NO.          LETTER

NO.

1          BLK             1A       A         27         BLU/BLK/WHT       14A          *D

2          WHT             1B       B         28         BLK/RED/GRN       14B          *E

3          RED             2A       C         29         WHT/RED/GRN       15A          *F

4          GRN             2B       D         30         RED/BLK/GRN       15B          *G

5          ORN             3A       E         31         GRN/BLK/ORN       16A          *H

6          BLU             3B       F         32         ORN/BLK/GRN       16B          *I

7          WHT/BLK         4A       G         33         BLU/WHT/ORN       17A          *J

8          RED/BLK         4B       H         34         BLK/WHT/ORN       17B          *K

9          GRN/BLK         5A       J         35         WHT/RED/ORN       18A          *M

10         ORN/BLK         5B       K         36         ORN/WHT/BLU       18B          *N

11         BLU/BLK         6A       L         37         WHT/RED/BLU       19A          *P

12         BLK/WHT         6B       M         38         BLK/WHT/GRN       19B          *Q

13         RED/WHT         7A       N         39         WHT/BLK/GRN       20A          *R

14         GRN/WHT         7B       P         40         RED/WHT/GRN       20B          *S

15         BLU/WHT         8A       R         41         GRN/WHT/BLU       21A          *T

16         BLK/RED         8B       S         42         ORN/RED/GRN       21B

17         WHT/RED         9A       T         43         BLU/RED/GRN       22A

18         ORN/RED         9B       U         44         BLK/WHT/BLU       22B

19         BLU/RED         10A      V         45         WHT/BLK/BLU       23A

20         RED/GRN         10B      W         46         RED/WHT/BLU       23B

21         ORN/GRN         11A      X         47         GRN/ORN/RED       24A

22         BLK/WHT/RED     11B      Y         48         ORN/RED/BLU       24B

23         WHT/BLK/RED     12A      Z         49         ORN/RED/BLU       25A

24         RED/BLK/WHT     12B      *A        50         BLK/ORN/RED       25B

25         GRN/BLK/WHT     13A      *B        51         WHT/BLK/ORN       26A

26         ORN/BLK/WHT     13B      *C        52         RED/ORN/BLK       26B

### TABLE 1 - COLOR CODE 1B (NEMA PUB. NO. WC 30, TABLE K-2)

The following standard color sequence should be used, instead of 1A, for cables that use yellow and brown

rather than white and green.  An A and B designation is given for use with paired cables.  A

"CABLE TERM. LETTER" is given for convenience for use with multi-pin connectors that are

wired following this standard color code sequence.  When there are more than 36 conductors (18) pairs,

some of the colors will be repeated and repeated.  In the latter cases, the lay or position of a wire in the

inner or outer layers must be considered to uniquely identify a conductor.

Used With CABLETYPE

8PR16TS	12PR16TS

16PR16TS	24PR16TS

36PR16TS	50PR16TS

12C12/3V	1PR16OS

UNPAIRED   **WIRE          PAIRED   CABLE     UNPAIRED   ** WIRE COLOR     PAIRED       CABLE

CABLE      COLOR           CABLE    TERM.     CABLE      CODE              CABLE PAIR   TERM.

COND NO.   CODE            PAIR     LETTER    COND. NO.                    NO.          LETTER

NO.

1          BLK             1A       A         19         ORN/BLU           10A          V

2          RED             1B       B         20         YEL/BLU           10B          W

3          BLU             2A       C         21         BRN/BLU           11A          X

4          ORN             2B       D         22         BLK/ORN           11BA         Y

5          YEL             3A       E         23         RED/ORN           12A          Z

6          BRN             3B       F         24         BLU/ORN           12B          *A

7          RED/BLK         4A       G         25         YEL/ORN           13A          *B

8          BLU/BLK         4B       H         26         BRN/ORN           13B          *C

9          ORN/BLK         5A       J         27         BLK/YEL           14A          *D

10         YEL/BLK         5B       K         28         RED/YEL           14B          *E

11         BRN/BLK         6A       L         29         BLU/YEL           15A          *F

12         BLK/RED         6B       M         30         ORN/YEL           15B          *G

13         BLU/RED         7A       N         31         BRN/YEL           16A          *H

14         ORN/RED         7B       P         32         BLK/BRN           16B          *I

15         YEL/RED         8A       R         33         RED/BRN           17A          *J

16         BRN/RED         8B       S         34         BLU/BRN           17B          *K

17         BLK/BLU         9A       T         35         ORN/BRN           18A          *M

18         RED/BLU         9B       U         36         YEL/BRN           18B          *N

* This letter is lower case on the connector

** The first color is the base color of the insulation.

### TABLE 1 - COLOR CODE 1C

The following color sequences can be applied to microphone cable and AC power cords:

Used With CABLE TYPE

2C16OS

2C22MS

3C12TYR

3C16TYR

CABLE      COLOR        TERM.     --OR--      CABLE       COLOR CODE      CABLE

COND NO.   CODE         LETTER                COND. NO.                   TERM.

LETTER

1          BLK          A                     1           BLK             A

2          WHT          B                     2           WHT             B

3          DRAIN        C                     3           GRN             C

### TABLE 1 - COLOR CODE 1D (BELDEN)

The following standard color sequence can be applied to individually shielded pairs with drain wires.

The "PAIR NO.", designation, 3A,3B and 3C, denotes that, associated with a pair

there are two insulated signal wires 3A and 3B, and one un-insulated drain wire 3C, that makes electrical

contact with the shield for that pair.  A "COND. NO." is assigned only for convenience and it

is useful only when each conductor, including the drain, is wired in sequence to a terminal block.  Note

that when RED is paired with BLK, the BLK is "PAIR NO." 1B, but when WHT is paired

with BLK, the BLK is "PAIR NO." 2B, etc.

USED WITH CABLE TYPE

3PR20IS

3PR22IS

6PR22IS

12PR22IS

19PR22IS

27PR24IS

6PR24IS

COND. NO     COLOR CODE   PAIR NO.     COND. NO     COLOR CODE    PAIR NO.     COND. NO.    COLOR CODE   PAIR NO.

1            RED          1A           28           BLU           10A          55           BLU          19A

2            BLK          1B           29           RED           10B          56           WHT          19B

3            DRAIN        1C           30           DRAIN         10C          57           DRAIN        19C

4            WHT          2A           31           YEL           11A          58           YEL          20A

5            BLK          2B           32           RED           11B          59           WHT          20B

6            DRAIN        2C           33           DRAIN         11C          60           DRAIN        20C

7            GRN          3A           34           BRN           12A          61           BRN          21A

8            BLK          3B           35           RED           12B          62           WHT          21B

9            DRAIN        3C           36           DRAIN         12C          63           DRAIN        21C

10           BLU          4A           37           ORN           13A          64           ORN          22A

11           BLK          4B           38           RED           13B          65           WHT          22B

12           DRAIN        4C           39           DRAIN         13C          66           DRAIN        22C

13           YEL          5A           40           WHT           14A          67           YEL          23A

14           BLK          5B           41           GRN           14B          68           BLU          23B

15           DRAIN        5C           42           DRAIN         14C          69           DRAIN        23C

16           BRN          6A           43           BLU           15A          70           BRN          24A

17           BLK          6B           44           GRN           15B          71           BLU          24B

18           DRAIN        6C           45           DRAIN         15C          72           DRAIN        24C

19           ORN          7A           46           YEL           16A          73           ORN          25A

20           BLK          7B           47           GRN           16B          74           BLU          25B

21           DRAIN        7C           48           DRAIN         16C          75           DRAIN        25C

22           WHT          8A           49           BRN           17A          76           YEL          26A

23           RED          8B           50           GRN           17B          77           BRN          26B

24           DRAIN        8C           51           DRAIN         17C          78           DRAIN        26C

25           GRN          9A           52           ORN           18A          79           ORN          27A

26           RED          9B           53           GRN           18B          80           BRN          27B

27           DRAIN        9C           54           DRAIN         18C          81           DRAIN        27C

### TABLE 1 - COLOR CODE 1E

The following color sequence can be applied to twisted pairs with an overall shield:

Used With CABLE TYPE

3PR22OS

COND.         COLOR          PAIR           TERM.         COND.          COLOR          PAIR           TERM.

NO.           CODE           NO.            LETTER        NO.            CODE           NO.            LETTER

1             BLK            1A             A             5              BRN            3A             E

2             WHT            1B             B             6              WHT            3B             F

3             RED            2A             C             7              DRAIN          OS             G

4             WHT            2B             D

### TABLE 1 - COLOR CODE 1F

Used With CABLE TYPE

1PR16AS	4PR16AS

4PR18TC	8PR16AS

16PR16AS	24PR16AS

24PR16TC	27PR22OS

50PR16AS	50PR16TC

The Cable contains twisted pairs. Each pair consists of a white (or red) wire and a black wire.

The white (or red) wire of the pair has a number imprinted on it and is the first or "A"

wire of the pair.  The black wire is the "B" wire of the pair. Thus, the white (or red) wires,

in general unless otherwise noted, go in numerical sequence onto the odd number terminal

block flags, and the black wires go onto the even number flags Also, the drain from the overall

shield is not connected unless specifically so instructed.

### TABLE 1 - COLOR CODE 1G

The following standard color sequence is to be used for the Magnet Mover cables.

A CABLE TERM LETTER is given for use with the 9-pin connectors used on the

Magnet-Mover cables (connector AMP9S).

Used With CABLE TYPE.

9C18J

UNPAIRED     WIRE          CABLE

CABLE.       COLOR         TERM.

COND.#       CODE          LETTER

1            BLK           A

2            RED           B

3            WHT           C

4            GRN           D

5            ORN           E

6            BLU           F

7            BRN           G

8            YEL           H

9            VIO           J

### TABLE 1 - COLOR CODE 1H

Used With CABLE TYPE

5PR20OS

PAIRED    ***WIRE      PAIRED       PAIRED    ***WIRE         PAIRED

CABLE.    COLOR        WIRE         CABLE.    COLOR           WIRE

COND.#    CODE         COND.#       COND.#    CODE            COND.#

1         WHT/BLK      1A,1B        15        BLK/BLU         15A,15B

2         WHT/BRN      2A,2B        16        BLK/VIO         16A,16B

3         WHT/RED      3A,3B        17        BLK/GRY         17A,17B

4         WHT/ORN      4A,4B        18        BRN/RED         18A,18B

5         WHT/YEL      5A,5B        19        BRN/ORN         19A,19B

6         WHT/GRN      6A,6B        20        BRN/YEL         20A,20B

7         WHT/BLU      7A,7B        21        BRN/GRN         21A,21B

8         WHT/VIO      8A,8B        22        BRN/BLU         22A,22B

9         WHT/GRY      9A,9B        23        BRN/VIO         23A,23B

10        BLK/BRN      10A,10B      24        BRN/GRY         24A,24B

11        BLK/RED      11A,11B      25        RED/ORN         25A,25B

12        BLK/ORN      12A,12B      26        RED/YEL         26A,26B

13        BLK/YEL      13A,13B      27        RED/GRN         27A,27B

14        BLK/GRN      14A,14B

*** The colors are for the pair of wires, i.e. pair 1 is WHT/BLK, meaning a white wire paired with a black wire.

### TABLE 1 - COLOR CODE 1J

CABLE TYPE

3PR24IS

18PR22OS

24PR16OS

4PR24IS

PAIRED     ***WIRE      CONNECTION      PAIRED     *** WIRE     CONNECTION

CABLE      COLOR CODE   BLOCK POINT #   CABLE      COLOR CODE   BLOCK POINT #

COND.#                                  COND.#

1          BLK/RED      1,2             15         GRN/BLU      29,30

2          BLK/WHT      3,4             16         GRN/YEL      31,32

3          BLK/GRN      5,6             17         GRN/BRN      33,34

4          BLK/BLU      7,8             18         GRN ORN      35,36

5          BLK/YEL      9,10            19         WHT/BLU      37,38

6          BLK/BRN      11,12           20         WHT/YEL      39,40

7          BLK/ORN      13,14

8          RED/WHT      15,16           21         WHT/BRN      41,42

9          RED/GRN      17,18           22         WHT/ORN      43,44

10         RED/BLU      19,20           23         BLU/YEL      45,46

24         BLU/BRN      47,48

11         RED/YEL      21,22           25  *      BLU/ORN      49,NC

12         RED/BRN      23,24           26  *      YEL/BRN      NC,NC

13         RED/ORN      25,26           27  *      YEL/ORN      NC,NC

14         GRN/WHT      27,28                      DRAIN        50

WIRE

* The 5 wires indicated as 'NC' are to be taped back against the

cable jacket. they are not used at this time.

*** The colors are for the pair of wires, i.e. pair 1 is BLK/RED,

meaning a black wire paired with a red wire.  The BLK wire

connects to terminal 1, and the RED to terminal 2.

### TABLE 1 - COLOR CODE 1K

PAIRED      ***WIRE       PAIRED WIRE  PAIRED CABLE  ***WIRE COLOR  PAIRED WIRE

CABLE.      COLOR CODE    COND.#       COND.#        CODE           COND.#

COND#.

1           WHT/BLU       1A,1B        15            BLK/GRY        15A,15B

2           WHT/ORN       2A,2B        16            YEL/BLU        16A,16B

3           WHT/GRN       3A,3B        17            YEL/ORN        17A,17B

4           WHT/BRN       4A,4B        18            YEL/GRN        18A,18B

5           WHT/GRY       5A,5B        19            YEL/BRN        19A,19B

6           RED/BLU       6A,6B        20            YEL/GRY        20A,20B

7           RED/ORN       7A,7B        21            VIO/BLU        21A,21B

8           RED/GRN       8A,8B        22            VIO/ORN        22A,22B

9           RED/BRN       9A,9B        23            VIO/GRN        23A,23B

10          RED/GRY       10A,10B      24            VIO/BRN        24A,24B

11          BLK/BLU       11A,11B      25            VIO/GRY        25A,25B

12          BLK/ORN       12A,12B

13          BLK/GRN       13A,13B

14          BLK/BRN       14A,14B

*** The colors are for the pair of wires, i.e. pair 1 is WHT/BLU, meaning a white wire paired with a blue wire.

### TABLE 1 - COLOR CODE 1L

The following color sequence applies. Colors are given in the sequence

of Body, First (wide) tracer, Second (narrow) tracer, and Third (narrow) tracer.

USED WITH CABLE TYPE

50C16/3V

50C16TC

4C18OS

3C16/3V

6C16OS

CABLE COND.  WIRE COLOR      CABLE       WIRE COLOR CODE     CABLE COND.   WIRE COLOR CODE

NO.          CODE            COND. NO.                       NO.

1            BLK             36          WHT/RED/GRN         71            WHT/BLK/GRN/ORN

2            RED             37          WHT/RED/BLU         72            WHT/BLK/GRN/GRY

3            WHT             38          WHT/RED/BRN         73            WHT/BLK/GRN/VIO

4            GRN             39          WHT/RED/VIO         74            WHT/BLK/YEL/BLU

5            ORN             40          WHT/GRN/BLK         75            WHT/BLK/YEL/BRN

6            BLU                                             76            WHT/BLK/YEL/ORN

7            BRN             41          WHT/GRN/RED         77            WHT/BLK/YEL/GRY

8            YEL             42          WHT/GRN/GRN         78            WHT/BLK/YEL/VIO

9            VIO             43          WHT/GRN/BLU         79            WHT/BLK/BLU/BRN

10           GRY             44          WHT/GRN/BRN         80            WHT/BLK/BLU/ORN

45          WHT/GRN/VIO

11           PNK             46          WHT/BLU/BLK         81            WHT/BLK/BLU/GRY

12           TAN             47          WHT/BLU/RED         82            WHT/BLK/BLU/VIO

13           RED/GRN         48          WHT/BLU/GRN         83            WHT/BLK/BRN/ORN

14           RED/YEL         49          WHT/BLU/BLU         84            WHT/BLK/BRN/GRY

15           RED/BLK         50          WHT/BLU/BRN         85            WHT/BLK/BRN/VIO

16           WHT/BLK                                         86            WHT/BLK/ORN/GRY

17           WHT/RED         51          WHT/BLU/VIO         87            WHT/BLK/ORN/VIO

18           WHT/GRN         52          WHT/BRN/BLK         88            WHT/BLK/GRY/VIO

19           WHT/YEL         53          WHT/BRN/RED         89            WHT/RED/BLK/GRN

20           WHT/BLU         54          WHT/BRN/GRN         90            WHT/RED/BLK/YEL

55          WHT/BRN/BLU

21           WHT/BRN         56          WHT/BRN/BRN         91            WHT/RED/BLK/BLU

22           WHT/ORN         57          WHT/BRN/VIO         92            WHT/RED/BLK/BRN

23           WHT/GRY         58          WHT/VIO/RED         93            WHT/RED/BLK/ORN

24           WHT/VIO         59          WHT/VIO/GRN         94            WHT/RED/BLK/GRY

25           WHT/BLK/RED     60          WHT/VIO/BLU         95            WHT/RED/BLK/VIO

26           WHT/BLK/GRN                                     96            WHT/RED/GRN/YEL

27           WHT/BLK/YEL     61          WHT/BLK/RED/GRN     97            WHT/RED/GRN/BLU

28           WHT/BLK/BLU     62          WHT/BLK/RED/YEL     98            WHT/RED/GRN/BRN

29           WHT/BLK/BRN     63          WHT/BLK/RED/BLU     99            WHT/RED/GRN/ORN

30           WHT/BLK/ORN     64          WHT/BLK/RED/BRN     100           WHT/RED/GRN/GRY

65          WHT/BLK/RED/ORN

31           WHT/BLK/GRY     66          WHT/BLK/RED/GRY

32           WHT/BLK/VIO     67          WHT/BLK/RED/VIO

33           WHT/BLK/BLK     68          WHT/BLK/GRN/YEL

34           WHT/RED/BLK     69          WHT/BLK/GRN/BLU

35           WHT/RED/RED     70          WHT/BLK/GRN/BRN

### TABLE 1 - COLOR CODE 1M

This cable is composed of solid colored wires, with a number for each wire printed on each wire.

The NUMBERS are to be followed to determine the connection order.

Listed below is a sample of one segment of this cable, AS AN EXAMPLE ONLY.  There is no

assurance that other segments will have the same colors associated with the same numbers.

USED WITH CABLE TYPE

19C12/6V

CABLE COND. NO.       WIRE COLOR CODE       CABLE COND. NO.   WIRE COLOR CODE

1                 	 BLK                11              	 BRN

2                 	 RED                12              	 BLK

3                 	 BLU                13              	 BLU

4                 	 ORN                14              	 ORN

5                 	 YEL                15              	 YEL

6                 	 BRN                16              	 BRN

7                 	 RED                17              	 BLK

8                 	 BLU                18              	 RED

9                 	 ORN                19              	 ORN

10                	 YEL

### TABLE 1 - COLOR CODE 1N

The following color sequence applies. Colors are given in the

sequence of Body, First (wide) tracer, Second (narrow) tracer,

and Third (narrow) tracer.

USED WITH CABLE TYPE

50C16/3V

27C20OS

CABLE COND.     WIRE COLOR CODE  CABLE COND. NO.  WIRE COLOR CODE    CABLE COND.    WIRE COLOR CODE

NO.                                                                  NO.

1               BLK              36               WHT/RED/YEL        71             WHT/BLK/ORN/VIO

2               BRN              37               WHT/RED/GRN        72             WHT/BLK/ORN/GRY

3               RED              38               WHT/RED/BLU        73             WHT/BLK/YEL/GRN

4               ORN              39               WHT/RED/VIO        74             WHT/BLK/YEL/BLU

5               YEL              40               WHT/RED/GRY        75             WHT/BLK/YEL/VIO

6               GRN                                                  76             WHT/BLK/YEL/GRY

7               BLU              41               WHT/ORN/YEL        77             WHT/BLK/GRN/BLU

8               VIO              42               WHT/ORN/GRN        78             WHT/BLK/GRN/VIO

9               GRY              43               WHT/ORN/BLU        79             WHT/BLK/GRN/GRY

10              WHT              44               WHT/ORN/VIO        80             WHT/BLK/BLU/VIO

45               WHT/ORN/GRY

11              WHT/BLK          46               WHT/YEL/GRN        81             WHT/BLK/BLU/GRY

12              WHT/BRN          47               WHT/YEL/BLU        82             WHT/BLK/VIO/GRY

13              WHT/RED          48               WHT/YEL/VIO        83             WHT/BRN/RED/ORN

14              WHT/ORN          49               WHT/YEL/GRY        84             WHT/BRN/RED/YEL

15              WHT/YEL          50               WHT/GRN/BLU        85             WHT/BRN/RED/GRN

16              WHT/GRN                                              86             WHT/BRN/RED/BLU

17              WHT/BLU          51               WHT/GRN/VIO        87             WHT/BRN/RED/VIO

18              WHT/VIO          52               WHT/GRN/GRY        88             WHT/BRN/RED/GRY

19              WHT/GRY          53               WHT/BLU/VIO        89             WHT/BRN/ORN/YEL

20              WHT/BLK/BRN      54               WHT/BLU/GRY        90             WHT/BRN/ORN/GRN

55               WHT/VIO/GRY

21              WHT/BLK/RED      56               WHT/BLK/BRN/RED    91             WHT/BRN/ORN/BLU

22              WHT/BLK/ORN      57               WHT/BLK/BRN/ORN    92             WHT/BRN/ORN/VIO

23              WHT/BLK/YEL      58               WHT/BLK/BRN/YEL    93             WHT/BRN/ORN/GRY

24              WHT/BLK/GRN      59               WHT/BLK/BRN/GRN    94             WHT/BRN/YEL/GRN

25              WHT/BLK/BLU      60               WHT/BLK/BRN/BLU    95             WHT/BRN/YEL/BLU

26              WHT/BLK/VIO                                          96             WHT/BRN/YEL/VIO

27              WHT/BLK/GRY      61               WHT/BLK/BRN/VIO    97             WHT/BRN/YEL/GRY

28              WHT/BRN/RED      62               WHT/BLK/BRN/GRY    98             WHT/BRN/GRN/BLU

29              WHT/BRN/ORN      63               WHT/BLK/RED/YEL    99             WHT/BRN/GRN/VIO

30              WHT/BRN/YEL      64               WHT/BLK/RED/GRN    100            WHT/BRN/GRN/GRY

65               WHT/BLK/RED/BLU

31              WHT/BRN/GRN      66               WHT/BLK/RED/VIO

32              WHT/BRN/BLU      67               WHT/BLK/RED/GRY

33              WHT/BRN/VIO      68               WHT/BLK/ORN/YEL

34              WHT/BRN/GRY      69               WHT/BLK/ORN/GRN

35              WHT/RED/ORN      70               WHT/BLK/ORN/BLU

### TABLE 1 - COLOR CODE 1P

USED WITH CABLE TYPE

15PR22OS

2PR22OS

3PR24IS

12PR22OS

9PR24IS

PAIRED   ***WIRE      PAIRED	    ***WIRE

CABLE    COLOR CODE   CABLE.      COLOR CODE

COND.#                COND.#

1        BLK/RED       15        GRN/BLU

2        BLK/WHT       16        GRN/YEL

3        BLK/GRN       17        GRN/BRN

4        BLK/BLU       18        GRN ORN

5        BLK/YEL       19        WHT/BLU

6        BLK/BRN       20        WHT/YEL

7        BLK/ORN

8        RED/WHT       21        WHT/BRN

9        RED/GRN       22        WHT/ORN

10       RED/BLU       23        BLU/YEL

24        BLU/BRN

11       RED/YEL       25        BLU/ORN

12       RED/BRN       26        BRN/YEL

13       RED/ORN       27        BRN/ORN

14       GRN/WHT

*** The colors are for the pair of wires, i.e. pair 1 is

BLK/RED, meaning a black wire paired with a red wire.  The

BLK wire connects to terminal 1, and the RED to terminal 2.

### TABLE 1 - COLOR CODE 1Q

Used With CABLE TYPE 3C20/3V  3C16FLX

4C16FLX  3C14FLX

CABLE     WIRE COLOR   CABLE   WIRE COLOR CODE

COND.     CODE         COND.

NO.                    NO.

1         BLK          20      ORN/BLU

2         RED          21      YEL/BLU

3         WHT          22      BRN/BLU

4         BLU          23      BLK/ORN

5         ORN          24      RED/ORN

6         YEL          25      BLU/ORN

7         BRN          26      YEL/ORN

8         RED/BLK      27      BRN/ORN

9         BLU/BLK      28      BLK/YEL

10        ORN/BLK      29      RED/YEL

11        YEL/BLK      30      BLU/YEL

12        BRN/BLK      31      ORN/YEL

13        BLK/RED      32      BRN/YEL

14        BLU/RED      33      BLK/BRN

15        ORN/RED      34      RED/BRN

16        YEL/RED      35      BLU/BRN

17        BRN/RED      36      ORN/BRN

18        BLK/BLU      37      YEL/BRN

19        RED/BLU

### TABLE 1 - COLOR CODE 1R

USED WITH CABLE TYPE

5PR20OS

COLOR    PAIR                      COLOR        PAIR

VAT7S    CODE     NO.    MS8S   VAT7S       CODE         NO.      MS8S

1        WHT      1A      A       5         WHT          3A        E

2        BLK      1B      B       6         RED          3B        F

3        WHT      2A      C       7         WHT          4A        G

4        BRN      2B      D       -         NONE         --        H

***The 5th pair (white/yellow) and the orange wire from the 4th

pair are not used - cut off.

### TABLE 1 - COLOR CODE 1S

USED WITH CABLE TYPE

2PR22IS

CABLE PAIR NO.     WIRE COLOR CODE

1A                 BLK

1B                 RED

2A                 BLK

2B                 WHT

DRAIN              BARE

### TABLE 1 - COLOR CODE 1T

USED WITH CABLE TYPE

16PR16IS

The cable contains twisted pairs. Each pair consists of a white

(or red), a black and a drain wire. Each white and

black conductor is printed with a pair number. The white wire

is the first of "A" wire. The black wire is the "B"

wire. The drain is the "C" wire. Wire in white, black,

drain sequence, starting with the first terminal indicated.

Repeat for each additional pair to be connected.

### TABLE 1 - COLOR CODE 1U

USED WITH CABLE TYPE

2C22MS

CABLE COND. NO.       WIRE COLOR CODE

1                 	 CLR

2                 	 BLK

3                		 RED

4                		 GRN

5                 	 BLU

### TABLE 1 - COLOR CODE 1V

Used With CABLE TYPE

12C20J

CABLE COND. NO.   WIRE COLOR CODE     CABLE COND. NO.       WIRE COLOR CODE

1                BLK              		 11                 PNK

2                WHT              		 12                 TAN

3                RED

4                GRN

5                BRN

6                BLU

7                ORN

8                YEL

9                VIO

10               GRY

### TABLE 1 - COLOR CODE 1W

USED WITH CABLE TYPE

7C22OS

CABLE COND. NO.     WIRE COLOR CODE

1                		BLK

2                 	RED

3                 	ORN

4                 	GRN

5                 	BLU

6                 	WHT

7                 	WHT/BLK

### TABLE 1 - COLOR CODE 1X

USED WITH CABLE TYPE

51PR22OS

PAIRED CABLE COND.#     WIRE COLOR CODE  PAIRED CABLE COND. #     WIRE COLOR CODE

1                     	BLK/RED             27                     BRN/YEL

2                    	BLK/WHT             28                     PUR/RED

3                    	BLK/GRN             29                     PUR/WHT

4                       BLK/BLU             30                     PUR GRN

5                       BLK/BRN             31                     PUR/BLU

6                       BLK/YEL             32                     PUR/BRN

7                       BLK/ORN             33                     PUR/YEL

8                       RED/GRN             34                     PUR/ORN

9                       RED/WHT             35                     PUR/SLA

10                      RED/BLU             36                     PUR/BLK

11                      RED/YEL             37                     SLA/RED

12                      RED/BRN             38                     SLA/WHT

13                      RED/ORN             39                     SLA/GRN

14                      GRN/BLU             40                     SLA/BLU

15                      GRN/WHT             41                     SLA/BRN

16                      GRN/BRN             42                     SLA/YEL

17                      GRN/ORN             43                     SLA/ORN

18                      GRN/YEL             44                     SLA/BLK

19                      WHT/BLU             45                     WHT-BLK/RED

20                      WHT/BRN             46                     WHT-BLK/GRN

21                      WHT/ORN             47                     WHT-BLK/BLU

22                      WHT/YEL             48                     WHT-BLK/BRN

23                      BLU/BRN             49                     WHT-BLK/YEL

24                      BLU/ORN             50                     WHT-BLK/ORN

25                      BLU/YEL             51                     WHT-BLK/PUR

26                      BRN/ORN

*** The colors are for the pair of wires, i.e. pair 1 is BLK/RED,

meaning a black wire paired with a red wire.  The

BLK wire connects to terminal 1, and the RED to terminal 2.

### TABLE 1 COLOR CODE 1Y

USED WITH CABLE TYPE

FIOPMM12

FIOPMM24

FIOPMM48

FIBER       COLOR                 FIBER           COLOR

1      	BLUE         		 7            RED

2           ORANGE        		 8            BLACK

3           GREEN                    9            YELLOW

4           BROWN                   10            VIOLET

5           SLATE                   11            DASHED BLUE

6           WHITE                   12            DASHED ORANGE

SPECIAL NOTE: CABLE CORE CONSISTS OF UP TO 8 BUNDLES, EACH CONTAINING

12 FIBERS. BUNDLES ARE IDENTIFIED BY COLOR-CODED YARN BINDERS. BINDER

COLOR CODE FOLLOWS SAME CODE AS FIBER COLOR CODE.

### TABLE 1 - COLOR CODE 1Z

USED WITH CABLE TYPE

25PR24OS

PIN       WIRE COLOR CODE         PIN

1     	 WHT/BRN             26

2     	 WHT/ORN             27

3     	 WHT/YEL             28

4     	 WHT/BLU             29

5     	 WHT/GRN             30

6     	 RED/BRN             31

7    		 RED/ORN             32

8      	 RED/GRN             33

9     	 RED/WHT             34

10    	 RED/BLU             35

11    	 RED/YEL             36

12    	 RED/BLK             37

13    	 BLU/ORN             38

14    	 BLU/BRN             39

15    	 BLU/YEL             40

16    	 BLU/GRN             41

17    	 BLU/BLK             42

18    	 BLK/ORN             43

19    	 BLK/GRN             44

20    	 BLK/BRN             45

21    	 BLK/WHT             46

22    	 BLK/YEL             47

23    	 GRN/YEL             48

24    	 GRN/BRN             49

25    	 GRN/ORN             50

*** The colors are for the pair of wires, i.e. pair 1 is WHT/BRN,

meaning a WHT wire paired with a BRN wire. The WHT wire

connects to terminal 1, and the BRN to terminal 26.

### TABLE 2Z – COLOR CODING OF FIBER OPTIC CABLES (In accordance with EIA/TIA-598)

Fiber Color 	Abbreviation		Buffer Tube Value	Fiber Value		Captar Coding

BLUE		BL			0			1			1

ORANGE	OR			12			2			2

GREEN		GR			24			3			3

BROWN		BR			36			4			4

SLATE		SL			48			5			5

WHITE		WH			60			6			6

RED		RD			72			7			7

BLACK		BK			84			8			8

YELLOW	YL			96			9			9

VIOLET	VL			108			10			A

ROSE		RO			120			11			B

AQUA		AQ			132			12			C

NOTE: To calculate the fiber numerical value, take the buffer tube value and add the fiber value.

For example, WH fiber in the YL buffer is actually fiber number 96+6=102.

NOTE: Captar coding for the fiber will be performed in two parts. One listing will be for the fiber

cable sheath. For coding the fiber to be used, code the fiber with the cable number and then the

Buffer  Tube Value and Fiber Value respectively. For example, using fiber 102 will get the coding

LC0XXXX96.

### TABLE 1 - COLOR CODE 1a

USED WITH CABLE TYPE

37C28FLT

PIN         WIRE COLOR CODE         PIN    WIRE COLOR CODE

1      	BRN                	 20      BLK

2       	RED                	 21      BRN

3       	ORN                	 22      RED

4       	YEL                	 23      ORN

5       	GR                 	 24      YEL

6       	BLU                	 25      GRN

7       	VIO                	 26      BLU

8       	GRY                	 27      VIO

9       	WHT                	 28      GRY

10      	BLK                	 29      WHT

11      	BRN                	 30      BLK

12      	RED                	 31      BRN

13      	ORN                	 32      RED

14      	YEL                	 33      ORN

15      	GRN                	 34      YEL

16      	BLU                	 35      GRN

17      	VIO                	 36      BLU

18      	GRY                	 37      VIO

19     	WHT

### TABLE 1 - COLOR CODE 1b

USED WITH CABLE TYPE

4PR24IS

PAIRED	WIRE

CABLE		COLOR

COND.#	CODE

1		BRN-WHT/BRN

2		ORN-WHT/ORN

3		GRN-WHT/GRN

4		BLU-WHT/BLU

### TABLE 1 - COLOR CODE 1c

CABLE	WIRE

COND.	COLOR

NO.	CODE

1	RED

2	GRN

| 568A Wiring |
| --- |
|  | Pair # Wire Pin # 1 - White/Blue White/Blue 5 Blue 4 2 - White/Orange White/Orange 3 Orange 6 3 - White/Green White/Green 1 Green 2 4 - White/Brown White/Brown 7 Brown 8 |  |

| 568B Wiring |
| --- |
|  | Pair # Wire Pin # 1) White/Blue White/Blue 5 Blue 4 2) White/Orange White/Orange 1 Orange 2 3) White/Green White/Green 3 Green 6 4) White/Brown White/Brown 7 Brown 8 |  |

### TABLE 2 - Cable Types and Cable Descriptions

GENERAL CABLE NOTE:

(n)-(cable-type):	(n) being a number larger than 1, means (n) runs of the indicated cable-type.

i.e.  '5-250MCM' would mean that 5 runs of 250 MCM conductor are to be

used to make up the indicated cable. Another example might be '12-#16'

meaning that 12 runs of  # 16 AWG wire (as specified below) are to

be used for the indicated cable. In this example, no wire color is specified,

implying that any color(s) may be used. The cable-plant coordination group is

to be informed of the color(s) actually used so that the related Installation

Schedule can then be up-graded to reflect the wiring as actually installed.

See color		Used with TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION									CODE TABLE		(See Table 3)

#(nn)-(ccc)		'(nn)' is the AWG # for a single conductor, concentric

stranded, insulated wire, UL types: RHH or RHW, FR-1 rated

THHN or THWN, or XHHN for aluminum wires.

Okonite type 'Okolon' (single conductor) or equal. Note that

AWG#0 through AWG#0000 will be indicated as 1/0 through 4/0, respectively.

For the MCM series cables, sizes are defined as follows.

The definitions are for copper, and aluminum.

These abbreviations are sometimes used where listing space

will not permit the complete descriptor.

250MCM:  25MCM   25MCAL											LB25D8

300MCM:  30MCM   35MCAL											LB30-6,LB30D6,LB30D8

350MCM:  35MCM   35MCAL											LB35-8,LB35D8

500MCM:  50MCM   50MCAL											LB50-8,LB50D8

535MCM:													LB53D8

600MCM:  60MCM   60MCAL											LB60D8

750MCM:  75MCM   75MCAL											LB75-8,LB75D8.

Unless otherwise specified, the conductor is copper. If it

is to be aluminum, the size is followed by the letters 'AL'.

For example, '3-#6AL' or '#2/0AL' indicates 3 runs of aluminum #6 AWG, or

1 run of aluminum #00 AWG, respectively.

'(ccc)' when included, is the color for the indicated conductor(s),

per table 1, above.

(Approximate outside diameter info, #12=0.1", #10=0.2",

#8=0.3",#6=0.3", #4=0.4", #2=0.5", #1=0.5",

1/0=0.6",2/0=0.6", 3/0=0.7", 4/0=0.7",

250MCMAL=0.733",350MCMAL=0.830",

500MCMAL=0.952",535MCM=1.3750",600MCMAL

=1.063",750MCMAL=1.159", 250MCM=0.85",

300MCM=0.82, 350MCM=0.96", 500MCM=1.10",

750MCM=1.32",1000MCM=1.47").

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

(nnn)MCM		Where (nnn) is the MCM size. See note under

'#(nn)-(ccc)' above.

(nnn)MCMAL		As above, except compact aluminum conductor. See note

under '#(nn)-(ccc)' above.

1010-100		10m CABLE, USED FOR TRANSVERSE TO AMPLIFIER.

MFR: METROLAB,S.A. VENDOR: GMW ASSOCIATES,REDWOOD CITY, CA.,

(650) 802-8292.

1011-3		3m CABLE, USED FOR TESLAMETER TO PROBE MULTIPLEXER. MFR:

METROLAB, S.A. VENDOR: GMW ASSOCIATES, REDWOOD CITY, CA.,

(650) 802-8292.

1080-2-7		7m CABLE, USED FOR PROBE, MINI TRANSVERSE, 0.09T TO

0.26T. MFR: METROLAB, S.A. VENDOR: GMW ASSOCIATES, REDWOOD

CITY, CA.,(650) 802-8292.

1080-4-7		7m CABLE, USED FOR PROBE, MINI TRANSVERSE, 0.35T TO

1.05T. MFR: METROLAB, S.A. VENDOR: GMW ASSOCIATES, REDWOOD

CITY, CA.,(650) 802-8292.

3076F			PROFIBUS PA NETWORKING CABLE. 18 AWG, 1 TWISTED PAIR,

OVERALL SHIELD. PVC JACKET. OD 0.280 in. 38lbs/1000ft. Belden 3076F 0031000. 300V

3079A			PROFIBUS DP NETWORKING CABLE. 22 AWG, 1 TWISTED PAIR,

OVERALL SHIELD, PVC JACKET,  OD 0.315 in, 52lbs/1000 ft.

Belden 3079A 0071000, 300V

1/0-FLEX		#1/0 AWG, FLEXIBLE LOCOMOTIVE CABLE, 275/24 STRANDS, 2000 VOLT.			LBR02-6,PP180C

SLAC P/N 61-329-601-16-A012.

1/0TLSNH		1/0, FLEX, 90 DEG / 105 DEG. C, TC, LOW SMOKE NON-HALOGEN (LSNH), 600V.

INSULATION COLOR: BLACK, 0.630” O.D.

AMERICAN INSULATED WIRE CORP P/N 39892

#2-FLEX		#2 AWG, EXTRA FLEXIBLE CABLE,150 STRAND, 600V,						LB2-5,-6

0.49" O.D., ALPHA NO. 7410

#2/0FLX		#2/0 AWG, EXTRA FLEXIBLE CABLE, 325 STRANDS, 600V,					LB03-8, LB03D8

0.65" O.D., ALPHA #7413

#4/0FLX		#4/0 AWG, EXTRA FLEXIBLE CABLE, 550 STRANDS, 600V,					LB049-3

0.81"O.D., ALPHA #7415										LB25D8, LB25-8

4/0TLSNH		4/0,FLEX, 90DEG/105DEG. C, TC,LOW SMOKE NON-HALOGEN(LSNH),				LB049-3, LB25D8

600V. INSULATION COLOR BLACK, 0.810" O.D.,AMERICAN P/N40032				LB25-8

AMERICAN INSULATED WIRE CORP P/N 39784.

#10CJ			SINGLE CONDUCTOR, #10 AWG, 113 STRAND, EXTRA FLEXIBLE

TINNED COPPER WIRE WITH A CLEAR JACKET.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

1/4HEL		1/4" FOAM DIELECTRIC, HELIAX COAXIAL CABLE,						N1/4HP

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,

0.29" O.D., 50 OHMS, ANDREW TYPE FHS1-50.

1/4HELA		1/4" AIR DIELECTRIC, HELIAX COAXIAL CABLE, JACKETED,

BRAIDED SHIELD CONSTRUCTION, 84147 RADIATION SENSING

CABLE, ANDREW TYPE 222793.

1/4HELB		1/4" HELIAX CABLE, AIR DIELECTRIC, 50 OHMS,						SHVMOD

0.29" O.D., ANDREW CAT. #HS1RP-50.

1/4HELS		1/4" FOAM DIELECTRIC, HELIAX COAXIAL CABLE,						N1/4HP

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,

PHASE STABILIZED, 50 OHMS, 0.29" O.D.

ANDREWS P/N 35422-11, FHJ1-50, OR FSJ1-50.

1/4HELSF		1/4" HELIAX, SUPERFLEXIBLE COAXIAL CABLE,							C41SW

FOAM DIELECTRIC, 50 OHMS, PHASE STABILIZED,

0.29" O.D., TYPE FSJ1-50A, ANDREW CAT.#35422-33.

1/4HSFX3	  	SET OF 3 EACH 1/4" HELIAX, SUPERFLEXIBLE COAXIAL

CABLE,FOAM N1/4HP DIELECTRIC, FIRE RETARDANT,50 OHMS,

PHASE MATCHED, 0.29" O.D.,ANDREW TYPE FSJ1RN-50B,

0.045 LB/FT.

1/2HEL		1/2" FOAM-DIELECTRIC, HELIAX COAXIAL CABLE,						N1/2HP, N1/2HJ

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,						SP1/2H

0.64" O.D., 50 OHMS, ANDREW TYPE LDF4-50.

1/2HELA		1/2" FOAM-DIELECTRIC, HELIAX COAXIAL CABLE,						N1/2HA

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,

0.64" O.D., 50 OHMS, ANDREW TYPE LDF4-50A.

1/2HELFR		1/2" HELIAX. SUPERFLEXIBLE COAXIAL CABLE,

NON-HALOGENATED, LLRF FIRE RETARDANT POLYOLEFIN.

FOAM PE, COPPER CLAD ALUMINUM WIRE,.53IN OD, GRAY,

CORRUGATED COPPER. 50 OHM ANDREWS P/N # FSJ4RN-50B

1/2HELGF		1/2" HELIAX COAXIAL CABLE, AIR DIELECTRIC, GAS-TIGHT.					N1/2HG, N1/2HD

0.58" O.D., ANDREWS P/N HJ4-50.

1/2HELS		SAME AS 1/2"HEL EXCEPT: PHASE STABILIZED, ANDREW 					N1/2HP, N1/2HJ

35422-14. OBSOLETE										SP1/2H

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

1/2HELSF		1/2" HELIAX, SUPERFLEXIBLE COAXIAL CABLE,FOAM						N1/2MH, N1/2HP

DIELECTRIC, 50 OHMS, PHASE STABILIZED, ANDREW

FSJ4-50B, TYPE #35422-24, 0.52" O.D.P

1/2RD			1/2" FOAM DIELECTRIC SEMI-RIGID JACKETED							S1/2RP, F1/2RP

COAXIAL CABLE, TIMES WIRE & CABLE NO. JT-4500J,

0.625" O.D., 75OHM, CATV SYSTEM CABLE.P

1/2RDB		1/2" FOAM DIELECTRIC SEMI-RIGID JACKETED							S1/2RP

COAXIAL CABLE, DIRECT BURIAL, TIMES WIRE & CABLE NO

JT-4500JB, 5/8" O.D., 75OHM, CATV SYSTEM CABLE.

3/4RGD		3/4" FOAM DIELECTRIC SEMI-RIGID JACKETED							S3/4RP

COAXIAL CABLE, TIMES WIRE & CABLE NO. JT-4750J, 7/8"

O.D.,75OHM, CATV SYSTEM CABLE.

3/8HEL		3/8" FOAM DIELECTRIC SEMI-RIGID, JACKETED, 						N3/8HP

COAXIAL CABLE, CORRUGATED COPPER OUTER CONDUCTOR,

0.44" O.D., 50 OHMS, ANDREW TYPE LDF2-50.

3/8HELFR		3/8" HELIAX. COAXIAL CABLE, NON-HALOGENATED, FIRE

RETARDANT, LLRF POLYOLEFIN. FOAM PE COPPER CLAD

ALUMINUM WIRE, GRAY, CORRUGATED COPPER OUTER CONDUCTOR,

.45” OD, 50 OHM ANDREWS P/N LDF2RN-50

3/8HELSF		3/8" EXTRA FLEXIBLE HELIAX CABLE, FIRE RETARDANT JACKET,				E2TSM (SMA3/8H)

ANDREWS P/N EFX2RN-50 OHM.

3/8HELX4		SPECIAL SET OF 4 EACH 3/8"HELIAX COAXIAL CABLES,					N3/8HF

TIMED, MATCHED AND LABELED FOR BEAM POSITION MONITORS.

TREATED AS A SINGLE CABLE.

5/8HELAN		5/8" (NOMINAL SIZE) HELIAX COAXIAL CABLE. COPPER OUTER

CONDUCTOR WITH ANNULAR CORRUGATION. 0.870 OD. LOW-SMOKE,

ZERO HALOGEN JACKET. ANDREW PART NUMBERS LDF4.5RK-50

(BLACK),LDF4.5RN-50 (GREY).

7/8HEL		7/8" FOAM DIELECTRIC, HELIAX COAXIAL CABLE,						N7/8HJ, SP7/8H

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,

1.1" O.D., 50 OHMS, ANDREW TYPE LDF5-50.

7/8HELGF		7/8" HELIAX COAXIAL CABLE,AIR DIELECTRIC, GAS-TIGHT.					N7/8GF

1.11" O.D.,ANDREWS P/N HJ5-50

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

7/8HELS		7/8" FOAM DIELECTRIC, HELIAX COAXIAL CABLE, 						N7/8HJ, SP7/8H

JACKETED, CORRUGATED COPPER OUTER CONDUCTOR,

PHASE STABILIZED, 50 OHMS, 1.1" O.D. ANDREWS

P/N 35422-15,LDF5-50A.

1”WCAL		WATER COOLED ALUMINUM CABLE, 1" DIAMETER, 						FLAG-1, FLAG-2

1.25" O.D., 1000VDC.

1.25HELS		1 1/4" HELIAX COAXIAL CABLE, FOAM DIELECTRIC,

50 OHM, 1.55" O.D.,15" MIN. RADIUS, ANDREWS P/N LDF6-50.

1C12T6V		ONE CONDUCTOR, #12AWG, TYPE THHN, 7 STRAND,600V.

SLAC S/N61-328-366-05

1C18E6V		ONE CONDUCTOR, #18AWG, BLACK TYPE E,STRANDED,600V.

SLAC S/N61-328-307-01

1C20RR6V		ONE CONDUCTOR, #20AWG INSULATED WIRE, RADIATION

RESISTANT, 600V, 0.1" O.D. MANCO WIRE AND CABLE CO.

UL-3271, #XML1030U(032).

1MTW-B		ONE CONDUCTOR, #1AWG, STRANDED, WIRE TYPE MTW, BLACK,

TFF, AWM, TEW, 600V, 500 FEET SPOOL.

1PR1T6V		ONE PAIR, #1AWG, STRANDED, TRAY CABLE, 600V,				1F

1.075" O.D., UNSHIELDED, ANIXTER CAT. #3G-0102.

1PR4T6V		ONE PAIR, #4AWG, STRANDED, TRAY CABLE, 600V				1F

0.787" O.D., UNSHIELDED, ANIXTER CAT. #3G-0402

1PR6T6V		ONE PAIR, #6AWG, STRANDED, TRAY CABLE, 600V,				1F

0.645" O.D., UNSHIELDED, ANXTER CAT. #3G-0602.

1PR16AS		ONE PAIR, ARMORED CABLE, 300V, #16 AWG, STRANDED,			1F		LSB#6, XLR3P

TINNED-COPPERWIRE, OVERALL SHIELD AND DRAIN WIRE,

0.24" O.D., TRAY CABLE, OKONITE CLX TYPE P-OS 564-10-3401.

1PR16OS		ONE PAIR, #16AWG, STRANDED, COPPER WIRE, OVERALL			1B		LFB, LSB#8, LFR

SHIELD, TRAY CABLE 0.301" O.D.,BELDEN CAT. #9342					MS10-A, MS10S,

MS3P, BP-02,

LRB#6, LRB3/8

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

1PR16T3V		ONE PAIR, #16AWG, 300V, UNSHIELDED, TRAY CABLE, 7-STRAND		1F		WNY, LFB, LSB#6

BARE SOFT ANNEALED COPPER, 0.26" O.D., OKONITE TYPE					XLR3S, XLR3P, MS10SA

P-NS, CAT. #260-10-4401.

1PR16TS		ONE PAIR, #16AWG, 600V, OVERALL SHIELDED, TYPE "T"

INSTRUMENTATION CABLE. 0.31" O.D. OKONITE#264-20-4401,

TYPE P-OS.

1PR16TZL		ONE PAIR, #16AWG, 300V, OVERALL SHIELDED, (BELDFOIL)

TEFZEL INSULATED, 0.212" O.D. BELDEN CAT#85231.

1PR18AS		ONE PAIR, ARMORED CABLE, #18AWG.

1PR18OS		ONE PAIR, #18AWG, 600V, STRANDED, OVERALL SHIELDED,			1F

0.279" O.D. TRAY CABLE, BELDEN CAT. #9341

1PR18TC		ONE PAIR, #18AWG, TRAY CABLE, OVERALL SHIELDED.

MFR: OKONITE.

1PR18T6V		ONE PAIR, #18AWG, STRANDED, TRAY CABLE, 600V,				1F		LFR, LSR#6

UNSHIELDED,0.276" O.D., BELDEN CAT. #9486.

1PR20OS		ONE PAIR, #20AWG, STRANDED, TINNED COPPER					1F		LRR#6,BP-02,LEMO4P,

CONDUCTORS, OVERALL SHIELDED, TRAY CABLE, 300 VOLT,					LFR,LSR,LFRM

0.217" O.D., BELDEN #9320									LRR1/4,LSR#6,TT4S

TT4P,TT12S,MS8P,

SOLDER,MS6P,MS3S

1PR20BH		ONE PAIR, #20AWG, STRANDED, COPPER WIRE, ALUMINUM FOIL

SHIELD, W/DRAIN WIRE BELDEN #9463, BLUE HOSE (TM)

ALLEN BRADLEY CAT# 1770 CD.

1PR20SCC	   ONE PAIR, #20 AWG, SOLID CONDUCTOR, CHROMEL (‘+’ OR YELLOW)

AND ALUMEL(‘-‘ OR RED) COLORED PAIRS WITH #22AWG BARE SOLID

CONDUCTOR DRAIN WIRE. ENCLOSED IN ALUMINIZED POLYESTER SHIELD

FOIL AND THEN A YELLOW, UL LISTED TYPE PLTC PVC JACKET,

RATED FOR 300V. 0.230" O.D., OMEGA P/N EXPP-K-20S-TWSH.

1PR22OS		ONE PAIR, #22AWG, STRANDED, COPPER WIRE, OVERALL			1L		LFR, TT19P, LSR#6

BELDFOIL SHIELDED, TRAY CABLE, 300 VOLT, 0.201" O.D.,					MS10SB, TT4P

BELDEN P/N 9322											TT12P, MS3S-S

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

1PR22PLT		ONE PAIR, #22AWG, EIA RS-485, STRANDED, OVERALL

BELDFOIL SHIELDED,PLTC TRAY CABLE, 300 VOLT,

0.284" O.D.,BELDEN P/N: 3105A

1PR22SR		ONE PAIR, #22AWG., TINNED COPPER, S-R PVC INSULATED,

TWISTED PAIR, BELDFOIL ALUM-POLY SHIELD, CHROME PVC JACKET,

300V, 0.186" O.D., BELDEN CAT#9462.

1PR22TEF		ONE TWISTED PAIR, #22 AWG, STRANDED TINNED COPPER,

TEFLON INSULATED, BELDFOIL SHIELDED, 0.118" O.D.,

BELDEN CAT. #82761.

1PR24CC		ONE PAIR, #24 AWG, COPPER CONSTANTAN, SOLID WIRE,

COPPER INNER INSULATION IS BLUE(POSITIVE) AND CONSTANTAN

INNER INSULATION IS RED(NEGATIVE), FIBERGLASS OVERALL

JACKET AND INNER INSULATION. ANSI TYPE "T", 0.050" X 0.080" O.D.

OMEGA CAT. #GG-T-24. CABLE TRAY APPLICATION: WHEN ROUTING

THIS THEMOCOUPLE WIRE IN A CABLE TRAY, PROTECT THE WIRE

OR WIRES USING INNERDUCT TUBING, MFG: SUPERFLEX, FLEXIBLE

SPLIT TUBING (GRAY – FLAME RETARDANT), ITEM #125-XXXXG.

1PR24DOS		ONE TWISTED PAIR, #24 AWG, EIA RS-485,

DOUBLE SHIELDED: FOIL AND BRAID WITH DRAIN WIRE,

300 VOLT, 0.232" O.D.MFG: BELDEN, P/N: 9841.

1PR24OS		TWINAX CABLE, ONE PAIR, #24AWG, STRANDED, 0.129"					LEMO-A

O.D., MIL-SPEC. MIL-C-17, BELDEN CAT. #81553

1PR24FRP		ONE PAIR, #24 AWG, STRANDED BARE COPPER CONDUCTORS,

WITH FLUOROCOPOLYMER .006" THICK INSULATION, FOIL

SHIELDED, PLENUM-RATED, RATED 150V, 0.114" O.D.

ALPHA CAT. #58401.

1PR24PLN		ONE PAIR, #24 AWG, PLENUM CABLE, NEC 725-(b), TINNED

COPPER, TEFLON INSULATED WITH BELDFOIL OVERALL SHIELD,

0.152" O.D., MFG BELDEN, P/N 88641.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

1PR28CC		ONE PAIR, #28 AWG, COPPER-CONSTANTAN SOLID WIRE,					STRIP, TC-CCP

COPPER INNER INSULATION IS BLUE(POSITIVE) AND						TC-CCS, TC-JNC

CONSTANTAN INNER INSULATION IS RED(NEGATIVE),						TC-SLV, W1, TCSCCP

WITH FIBERGLASS OVERALL JACKET, ANSI TYPE 'T',

OMEGA CAT-# GG-T-28, 0.045" X 0.070"O.D.

CABLE TRAY APPLICATION: WHEN ROUTING THIS THEMOCOUPLE

WIRE IN A CABLE TRAY, PROTECT THE WIRE OR WIRES USING

INNERDUCT TUBING, MFG: SUPERFLEX, FLEXIBLE SPLIT TUBING

(GRAY – FLAME RETARDANT), ITEM #125-XXXXG.

1RMMTLN		   1-RIBBON, (12-STRAND), 50/125uM LASER-OPTIMIZED,

MULTI-MODE FIBER, (550M @ 10 GIGABIT), LOW-SMOKE,

ZERO-HALOGEN JACKET. CORNING PART NUMBER 012TCZ-14190-20.

1RSMTLN		   1-RIBBON, (12-STRAND), 9/125uM, SINGLE-MODE FIBER OPTIC

CABLE, LOW-SMOKE, ZERO HALOGEN JACKET.  CORNING PART

NUMBER 012ECZ-14101-20.

1THHN		   ONE CONDUCTOR, #1 AWG, THHN, BLACK, 19 STRAND, 600V.

SLAC S/N 61-328-373-01.

1TPR22OS		ONE TWISTED PAIR, #22AWG, OVERALL SHIELDED.

2/0 WELD		#2/0 WELDING CABLE.

2/0TLSNH		2/0, 90DEG/105DEG. C, TC, LOW SMOKE NON-HALOGEN						LB3/0

(LSNH), 600V.INSULATION COLOR BLACK, 0.740" O.D.,

AMERICAN PART # 40026.

250WELD		250MCM WELDING CABLE. ONE COPPER CONDUCTOR # 250 KCM,

FLEXIBLE WELDING CABLE, THERMOSET JACKETTED, CLASS K

ROPE STRANDED,(2450 STRANDS) 105 DEGREES "C", 0.925 O.D.,

ANIXTER CAT # 5J-2501

2C1TLSNU     	TWO CONDUCTOR,#1AWG,600V,19 STRAND,UNSHIELDED, 90DEG. C, LOW SMOKE

NON-HALOGENATED (LSNH), POWER TRAY CABLE, TC, 1.050" O.D.,

NO DRAIN WIRE. LAKE CABLE P/N VXH12.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C2TLSNH		TWO CONDUCTOR #2 AWG 19 STRAND,SHIELDED,AVERAGE INSULATION 				LB2D6, LB206S

THICKNESS 45 MILS, AVERAGE JACKET THICKNESS 80 MILS, NOMINAL

CABLE O.D. 0.975 IN, NOMINAL CABLE WEIGHT 680 LBS/1000 FT.

MULTI-CONDUCTOR, 600V, HEAT, MOISTURE, AND SUNLIGHT RESISTANT,

BLACK, POLYOLEFIN OR EQUIVALENT LOW SMOKE ZERO HALOGENATED

INSULATING MATERIAL, WET OR DRY LOCATION AT 90 DEGREES C.

PART # DRAKA 400287. LAKE CABLE P/N VXH22S(19)(W/DRAIN WIRE)

2C2TLSNU		TWO CONDUCTOR,#2AWG,600V,19 STRAND,UNSHIELDED, 90DEG. C,

TC,LOW SMOKE NON-HALOGENATED (LSNH),WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE) INSULATED CIRCUIT

CONDUCTORS AND CROSS-LINKED POLYOLEFIN(XLPO)JACKET,0.918"

O.D., NO DRAIN WIRE. LAKE CABLE P/N VXH22(19).

2C2T6V		TWO CONDUCTORS, #2AWG, STRANDED, PVC/NYLON PVC				1F

CONTROL CABLE, UNSHIELDED, TRAY CABLE, 90 DEGREE C,

600V, 0.787" O.D., ANIXTER CAT. #3G-0202

2C2TS6V		TWO CONDUCTORS,#2AWG,COPPER CONDUCTORS, 600V, 90C TRAY-RATED,			LB2-5

XLPE BLACK INSULATION (BLACK AND WHITE INDIVIDUAL CONDUCTORS),

UV RESISTANT (SUN RESISTANT). O.D.= 0.975 MANUFACTURER:

TAMAQUA CABLE(MANCO P/N M0202/7 XL02G).

2C4T6V		TWO CONDUCTORS, #4AWG, STRANDED, PVC/NYLON PVC				1F

CONTROL CABLE, UNSHIELDED, TRAY CABLE, 90 DEGREE C, 600V,

0.787" O.D., ANIXTER CAT. #3G-0402.

2C6LSNH           NUMBER & CIRCUIT CONDUCTOR SIZE 2C/#6 AWG, AVERAGE

INSULATION THICKNESS 45 MILS, AVERAGE JACKET THICKNESS

60 MILS, NOMINAL CABLE 0.775" O.D. NOMINAL CABLE WEIGHT

378 LBS/1000 FT. MULTI-CONDUCTOR, 600V, HEAT, MOISTURE

AND SUNLIGHT RESISTANT, BLACK, POLYOLEFIN OR EQUIVALENT

LOW SMOKE HALOGENATED INSULATING MATERIAL. WET OR DRY LOCATION

AT 90 DEGREES C. PART # DRAKA 382559

2C4TLN		TWO CONDUCTOR, #4AWG,19 STRAND,SHIELDED,90DEG. C, TC,

LOW SMOKE NON-HALOGENATED(LSNH), WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN (XLPO) JACKET, 600V 0.75" O.D.

LAKE CABLE P/N VXH42S(19) (W/DRAIN WIRE)

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C4TLNU		TWO CONDUCTOR, #4AWG,600V,19 STRAND,UNSHIELDED, 90DEG. C, TC,

LOW SMOKE NON-HALOGENATED(LSNH), WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN (XLPO) JACKET, 0.771" O.D., NO

DRAIN WIRE. LAKE CABLE P/N VXH42(19).

2C6LSNH		NUMBER & CIRCUIT CONDUCTOR SIZE 2C/#6 AWG, AVERAGE INSULATION

THICKNESS 45 MILS, AVERAGE JACKET THICKNESS 60 MILS, NOMINAL

CABLE O.D. 0.775 IN,NOMINAL CABLE WEIGHT 378 LBS/1000 FT.

MULTI-CONDUCTOR, 600V, HEAT, MOISTURE AND SUNLIGHT RESISTANT,

BLACK, POLYOLEFIN OR EQUIVALENT LOW SMOKE HALOGENATED

INSULATING MATERIAL. WET OR DRY LOCATION AT 90 DEGREES C.

PART # DRAKA 382559

2C6T6V		TWO CONDUCTORS, #6AWG, STRANDED, PVC/NYLON PVC				1F

CONTROL CABLE, UNSHIELDED, TRAY CABLE, 90 DEGREE C, 600V,

0.645" O.D., ANIXTER CAT. #3G-0602.

2C6T6VOS		TWO COPPER CONDUCTORS, #6AWG, TYPE C  STRANDED (19 STRANDS)		1F		LR6#10S

XLPE,BLACK,SHIELDED, UV RESISTANT (SUN RESISTANT),

90 DEGREES C, 600V,0.775 O.D. WIRE(CU) O.D.0.275.

2C8T6V		TWO CONDUCTORS, #8AWG, STRANDED PVC/NYLON PVC CONTROL			1F

CABLE, UNSHIELDED TRAY CABLE, 90 DEGREE C, 600V, 0.567"

O.D., ANIXTER CAT. #3G-0802.

2C8TLN		TWO CONDUCTOR,#8 AWG, 19 STRAND,SHIELDED,90DEG.C,TC,

LOW SMOKE NON-HALOGENATED(LSNH),WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE (XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN(XLPO)JACKET,600V. 0.630" O.D.,

DRAKA CABLETEQ P/N LATER,MANCO PART # D88930208, Quote

# TCP8893 LAKE CABLE P/N VXH82S(19),(W/DRAIN WIRE)

2C8TLNU		TWO CONDUCTOR,#8AWG,600V,19 STRAND,UNSHIELDED,90DEG.C,TC,

LOW SMOKE  NON-HALOGENATED(LSNH),WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN(XLPO)JACKET, 0.597" O.D., NO DRAIN

WIRE. LAKE CABLE P/N VXH82(19).

2C8TYR		TWO CONDUCTORS, TYREX SO, 600V, #8AWG, STRANDED,			1C		LR8-6, PS50/2

COPPER WIRE, 0.70" O.D., STANDARD WIRE & CABLE CO.

CAT. #705-5. NOT FOR CABLE TRAY USE.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C10T6V		TWO CONDUCTORS, #10AWG, STRANDED, PVC/NYLON PVC				1B

CONTROL CABLE, UNSHIELDED, TRAY CABLE, 90 DEGREE C,

0.262 X 0.431" O.D.,600V ANIXTER CAT. #2A-1002.

2C10TC		TWO CONDUCTORS, #10AWG,600V,CONTROL TRAY CABLE.

O.47" O.D. OKONITE CAT#202-10-4502.

2C10TLN		TWO CONDUCTOR,#10 AWG, 19 STRAND,SHIELDED,90DEG. C, TC,

LOW SMOKE NON-HALOGENATED (LSNH), WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE (XLPE) INSULATED CIRCUIT

CONDUCTORS AND CROSS-LINKED POLYOLEFIN (XLPO) JACKET,

600V 0.5" O.D. LAKE CABLE P/N VXH102S(19). (W/DRAIN WIRE)

2C10TLNU		TWO CONDUCTOR,#10AWG,600V,19 STRAND, UNSHIELDED, 90DEG. C, TC,

LOW SMOKE NON-HALOGENATED(LSNH),WITH THERMOSETTING CROSS-LINKED

POLYETHYLENE (XLPE) INSULATED CIRCUIT CONDUCTORS AND

CROSS-LINKED POLYOLEFIN(XLPO)JACKET,0.449" O.D., NO DRAIN WIRE,

LAKE CABLE P/N VXH102(19).

2C10TYR		TWO CONDUCTORS, TYREX TYPE SO, 600V, #10AWG,				1A		LSY#8, STRIP

STRANDED, COPPER WIRE 0.640" O.D., STANDARD WIRE &

CABLE CO. CAT. #703-26. NOT FOR CABLE TRAY USE.

2C12OS		TWO CONDUCTORS, #12AWG, STRANDED, 600V, WITH OVERALL			1A		LRY#6, PPR8

SHIELD AND JACKET, TYPE SJO500, PER MIL-C-3432D, C0-02-MFG

(2/12) SJO500, 0.50" O.D.

2C12RR		TWO CONDUCTORS, #12AWG, RADIATION RESISTANT,						MS8RPA

INDIVIDUAL WIRE. BAY ASSOCIATES MIL-16878/15-12. STYLE 3271.

2C12TC		TWO CONDUCTORS, #12AWG, 600V, CONTROL TRAY CABLE.

0.42" O.D. OKONITE CAT#202-10-4402.

2C12T6V		TWO CONDUCTORS, #12AWG, UNSHIELDED, STRANDED,				1B

PVC/NYLON CONTROL CABLE TRAY CABLE, 90 DEGREE C, 600V,

0.227 X 0.361" O.D., ANIXTER CAT. #2A-1202.

2C12TEF		TWO CONDUCTORS, #12AWG, TINNED COPPER, TEFLON

INSULATED. CONDUCTORS CABLED. BELDFOIL ALUMINUM.

POLYESTER SHIELD TEFLON JACKET, RED TINT. NEC ARTICLE

760. PLENUM-POWER LIMITED. 0.303"O.D. BELDEN P/N83802.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C12TLN		TWO CONDUCTORS,#12AWG, TYPE C STRAND, 90DEG. C, TC,

LOW SMOKE NON-HALOGENATED(LSNH), WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT

CONDUCTORS AND CROSS-LINKED POLYOLEFIN (XLPO)

JACKET, 600V 0.415" O.D.,DRAKA CABLETEQ PART# LATER,

MANCO PART # D88930212, Quote # TCP8893

2C12TLNU		TWO CONDUCTOR,#12AWG,600V,19 STRAND,UNSHIELDED, 90DEG. C,

TC, LOW SMOKE NON-HALOGENATED (LSNH),WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN(XLPO)JACKET,0.394" O.D.,

NO DRAIN WIRE. LAKE CABLE P/N VXH122(19).

2C12TYR		TWO CONDUCTOR, TYREX TYPE SO, 600V, #12AWG,				1A		LFY, STRIP

STRANDED, COPPER WIRE 0.605" O.D., STANDARD WIRE &					LSY#8,MS8PAR,

CABLE CO. CAT. #703-20 NOT FOR CABLE TRAY USE.						LRY#8

2C14OS		TWO CONDUCTORS, #14AWG, OVERALL SHIELDED.

2C14TYR		TWO CONDUCTORS, TYREX TYPE SO, 600V, #14AWG,				1A		LRB#6, STRIP

STRANDED COPPER WIRE 0.53" O.D., STANDARD WIRE &

CABLE CO. CAT. #703-14. NOT FOR CABLE TRAY USE.

2C16T3V		TWO CONDUCTORS, #16AWG, 300V. MFR: BELDEN.

2C16T6V		TWO CONDUCTORS, #16AWG, 600V, 19 TC STRANDS,

TRAY CABLE. 0.301" O.D. BELDEN CAT#9487.

2C18OTN		TWO CONDUCTORS, 18 AWG, SHIELDED, LOW SMOKE ZERO

HALOGEN, 300V, TRAY CABLE, O.D. 0.313 IN., LAKE CABLE

P/N: TXH182S.

2C18TC		TWO CONDUCTORS, #18AWG, TRAY CABLE.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C18TLN		TWO CONDUCTORS,18AWG,19 STRAND,OVERALL SHIELD,TRAY CABLE,

600V CONDUCTOR,18 AWG TIN COATED COPPER. CLASS B

STRANDING PER ASTM B8 INSULATION. CROSS-LINKED

POLYETHYLENE(XLPE).COLOR CODE: ONE BLACK AND

ONE WHITE. CONDUCTOR SHIELD: BRAIDED TIN COATED

COPPER SHIELD OVER INDIVIDUAL PAIRS. COLOR CODE:

METHOD 2(OVER COMP SHIELD).JACKET: LOW SMOKE,

ZERO-HALOGEN CROSS-LINKED POLYOLEFIN(LSZH XL POLYO).

BLACK (BLK) OR WHITE (WHT) CABLES ARE 75 OHM INDIVIDUALLY

SHIELDED. MULTI-PAIR CONSTRUCTIONS SUITABLE FOR WATERTIGHT,

NON-FLEXING SERVICE. MIL-C-24643/33, TYPE LS2SWU-1,

O.D.=0.295. LAKE CABLE P/N VXH182S(19) (W/DRAIN WIRE)

2C18TLNU		TWO CONDUCTOR,#18AWG,600V,19 STRAND,UNSHIELDED, 90DEG. C,

TC, LOW SMOKE NON-HALOGENATED (LSNH),WITH THERMOSETTING

CROSS-LINKED POLYETHYLENE(XLPE)INSULATED CIRCUIT CONDUCTORS

AND CROSS-LINKED POLYOLEFIN(XLPO)JACKET,0.305" O.D.,

NO DRAIN WIRE. LAKE CABLE P/N VXH182(19).

2C20OS		TWO CONDUCTORS, #20AWG, 300V, STRANDED TINNED

COPPER CONDUCTORS, OVERALL SHIELDED, PVC JACKET,

0.18" O.D., ALPHA CAT#2412.

2C20OSTC		TWO CONDUCTORS # 20AWG OVERALL SHIELDED, TRAY RATED

CABLE, STRANDED COPPER WIRE, 300V, UV RESISTANT,

0.207" O.D., PLTC CABLE ALPHA, ID SWITCH.

CAT # 5610B2001E OR EQUAL.

2C20RR		TWO CONDUCTOR, #20AWG, STRANDED, RADIATION AND				1F		SOLDER

CORROSION, RESISTANT FLAME RETARDANT, NON-PVC, ITT-

SURPRENANT XML-SERIES, 600VAC ARE TWISTED TOGETHER

USING SLAC S/N61-328-316-01 BLACK AND SLAC S/N61-328-316-10

WHITE. 0.10" O.D.

2C22MS		TWO CONDUCTORS, MICROPHONE CABLE, #22AWG,					1U		LSR#6, TT4P,

STRANDED, TINNED-COPPER WIRE, OVERALL SHIELD WITH DRAIN				TT4S, TT8S

WIRE, 0.23" O.D., BELDEN CAT. #8422								MS3P, MS3S,

LFR, LEMO-A,LRR#6

2C22OLN		TWO CONDUCTOR,22 AWG, SHIELDED, LOW SMOKE NON-HALOGEN,

CABLE TRAY RATED.0.190” O.D.,LAKE CABLE P/N: TXH222S.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2C22OS		TWO CONDUCTORS OVERALL SHIELDED, #22AWG

THERMOCOUPLE. HAL 10443P. EX PP-K-20S-TWSH-SLE.

OMEGA ENGINEERING.

2C250LV		TWO(250Kcmil)CABLES, EP INSULATION/HYPALON JACKET,

90deg.DRY/75deg.WET, 600V, 0.96" O.D., ANIXTER CAT#3BF-2501

OR EQUIVALENT.

2C500TLS		PARALLEL RUN OF 2 SINGLE CONDUCTOR 500KCMIL, FLEX,					LB60D8, LB60-8

90DEG/105DEG. C, TC,LOW SMOKE NON-HALOGEN, (LSNH) 600V.

INSULATION COLOR GRAY, 1.150IN O.D.WT= 1.775LB/FT AMERICAN

P/N 39778. AMERICAN INSULATED WIRE CORP P/N 39914 BLACK

INSULATION.

2MTW-B		ONE CONDUCTOR, #2AWG, STRANDED, WIRE TYPE MTW, BLACK,

TFF, AWM, TEW, 600V, 500 FEET SPOOL.

2PR16AS		TWO PAIRS, #16AWG, CLX CABLE, OVERALL SHIELDED.

MFR: OKONITE.

2PR16IS		TWO PAIRS, #16AWG, INDIVIDUAL SHIELDED AND OVERALL			1A

SHIELD, STRANDED TINNED COPPER, 300V, TRAY CABLE, ANIXTER

P/N 323-231-1602.

2PR16XS		TWO PAIRS, #16AWG, INDIVIDUAL SHIELDED AND OVERALL, SHIELD,

STRANDED TINNED COPPER, 300V, TRAY CABLE, LSZH, OD: 0.401 in. 109 Lbs/Mft.

USE Lake Cable P/N: TXH162SPOS.

2PR18OS		TWO TWISTED PAIRS, #18AWG, STRANDED, OVERALL				1F		LFR, TT8S

SHIELD, 300V, TRAY CABLE, 0.397" O.D., BELDEN CAT. #9552.

2PR18IS		TWO PAIRS, #18AWG, INDIVIDUAL SHIELDED.

2PR18XS		TWO PAIRS, #18AWG, INDIVIDUAL SHIELDED. OVERALL SHIELD,

LSZH, 300 VOLT, LSZH, OD: 0.343 in. 72 Lbs/Mft. USE Lake Cable P/N: TXH182SPOS.

2PR20IS		TWO TWISTED PAIRS, #20AWG, STRANDED, INDIVIDUALLY			1S

SHIELDED, WITH #22 AWG DRAIN WIRE, 300 VOLT, CM RATED,

0.30" O.D., BELDEN P/N 9402.

2PR20OS		TWO PAIRS, #20 AWG, 300V, OVERALL SHIELDED, TRAY			1H

CABLE, 0.27" O.D., ALPHA CAT. #45452.

2PR20XS		TWO TWISTED PAIRS, #20AWG, STRANDED, INDIVIDUALLY SHIELDED, OVERALL SHIELD,

WITH #22 AWG DRAIN WIRE, 300 VOLT, LSZH, OD: 0.338 inches.

64 Lbs/Mft. CABLE P/N: TXH202SPOS

2PR20OTN		TWO PAIRS, #20 AWG, 300V, OVERALL SHIELDED, TRAY CABLE,		1H

LOW SMOKE ZERO HALOGEN, 0.27” O.D.

LAKE CABLE P/N: TXH202PRS.

2PR20SCC		TWO RUNS OF 1PR20SCC.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2PR22IS		TWO TWISTED PAIRS, #22AWG, STRANDED, INDIVIDUALLY			1S		LFR

SHIELDED,WITH #24 AWG STRANDED COMMON DRAIN WIRE, 300

VOLT, 0.16" O.D., CM RATED, BELDEN P/N 8723.

SLAC SN61-329-314-02.

2PR22OS		TWO TWISTED PAIRS, 300V, #22AWG, STRANDED, COPPER			1F		LSR, TT4S

WIRE, OVERALL SHIELD WITH DRAIN WIRE, 0.31" O.D. TRAY CABLE.			DB9P AMP4P,AMP4S

2PR22OTN		2 PAIR, 22 AWG STRANDED CABLE, OVERALL SHIELD WITH

DRAIN WIRE AND LSZH JACKET, LAKE CABLE P/N TXH222PRS.

2PR22SS		TWO PAIR, #22AWG, SOLID CONDUCTORS, 300V, 0.168"			1c

O.D., CM RATED, BELDEN CAT. #8795.

2PR22TX2		FOUR CONDUCTORS, #22AWG, STRANDED, TWISTED PAIRS,

INDIVIDUALLY SHIELDED, WITH #24AWG STRANDED TC DRAIN WIRE,

300 VOLT, 0.196" O.D., BLACK LSZH JACKET. BELDEN PN# 8723SB.

2PR24IS		TWO PAIRS, STRANDED COPPER WIRE, INDIVIDUALLY				1P		DAY-20, MS6S

SHIELDED WITH ONE ISOLATED DRAIN WIRE PER PAIR, CHROME				MS6PR, LFR

PVC JACKET, 0.335"O.D., CM RATED BELDEN CAT-# 9729					RTDS

'DATALENE' CABLE.

2PR24OS		TWO PAIRS, #24AWG, OVERALL SHIELDED, STRANDED TWISTED,

POLYETHYLENE INSULATED. TINNED COPPER, TRAY RATED.

BELDEN CAT#9842.

2PR28OS		TWO TWISTED PAIRS, #28AWG, STRANDED TINNED COPPER

DRAIN WIRE. OVERALL SHIELDED, 0.235" O.D., CHROME PVC

JACKET. BELDEN CAT#8132.

2SMMTLN		2-STRAND, 50/125UM, (550 METER 10-GBE), MULTI-MODE,

OPTICAL BREAKOUT CABLE.  LOW-SMOKE, ZERO-HALOGEN

CABLE SUITABLE FOR TRAYS AND RISERS. AQUA OUTER JACKET.

OUTER DIAMETER: 7.8MM(.31").  SUB-CABLE DIAMETER: 2.5MM(.10").

MINIMUM INSTALLATION BEND RADIUS: 11.7CM(4.6").

MINIMUM LONG-TERM BEND RADIUS: 7.8CM(3.1").

OPTICAL CABLE CORPORATION PART NUMBER: BX002ZALE9QZ

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2SSMTLN		2-STRAND, 9/125UM, SINGLE-MODE, OPTICAL BREAKOUT CABLE.

LOW-SMOKE, ZERO-HALOGEN CABLE SUITABLE FOR TRAYS AND RISERS.

YELLOW OUTER JACKET. OUTER DIAMETER: 7.8MM(.31").

SUB-CABLE DIAMETER: 2.5MM(.10"). MINIMUM INSTALLATION BEND

RADIUS: 11.7CM(4.6").  MINIMUM LONG-TERM BEND RADIUS: 7.8CM(3.1").

OPTICAL CABLE CORPORATION PART NUMBER: BX002ZSLB9YZ

2THHN		   ONE CONDUCTOR, #2 AWG, THHN, BLACK, 19 STRAND, 600V.

SLAC S/N 61-328-372-01.

2T1C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C1TLSNU.

2T2C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C2TLSNU.

2T4C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C4TLNU.

2T6VOJ		SLAC CABLE TYPE USED FOR CODING PURPOSE ONLY. THE CONDUCTOR				LB2-5

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE 2C2TS6V.

2T8C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C8TLNU.

2T10C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C10TLNU.

2T18C1		   SLAC CABLE TYPE USED FOR CODING PURPOSES ONLY. THE CONDUCTOR

BELONGS TO ONE PAIR CABLE AND IS USED TO CONNECT MAGNETS

IN SERIES. THIS PARTICULAR CONDUCTOR BELONGS TO SLAC TYPE

CABLE: 2C18OTN.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

2.0HEL		1 5/8" HELIAX COAXIAL CABLE, FOAM DIELECTRIC, STANDARD JACKET,			N-PLIC

50 OHMS,1.98" OD, COPPER CONDUCTOR, ANDREW TYPE LDF7-50A.

BCS MPS PLIC

3C2T6V		THREE CONDUCTORS, #2AWG, STRANDED, PVC/NYLON PVC

CONTROL CABLE, UNSHIELDED, TRAY CABLE, 90 DEGREE C,

600V, 0.947" O.D., ANIXTER CAT. #3G-0203

3C4IW			THREE CONDUCTORS, #4AWG INDIVIDUAL WIRE.

3C8T6V		THREE CONDUCTORS, #8AWG, 600V, PVC JACKET. STRANDED

COPPER WIRES. 0.600" O.D. TRAY CABLE. ANIXTER #3G-0803.

3C10PVC		THREE CONDUCTORS, PVC JACKET AND INSULATION, 600V, #10 AWG,

FLEXIBLE STRANDED COPPER WIRE, LAPPUSA OLEFLEX 190

P/N 601003 NOT FOR CABLE TRAY USE

3C10STOW	   THREE CONDUCTORS, PVC JACKET AND INSULATION TYPE STOW,

600V, #10 AWG,FLEXIBLE STRANDED COPPER WIRE, COLEMAN

CABLE P/N 20039 NOT FOR CABLE TRAY USE.

3C10TYR		THREE CONDUCTORS, TYREX TYPE SO, 600V, #10 AWG,				1C

STRANDED,COPPER WIRE, 0.69" O.D., SLAC SN61-329-722-42.

NOT FOR CABLE TRAY USE.

3C12FLX		THREE CONDUCTORS, #12AWG, 600V, MFR: AMERICAN

FLEX CONDUIT.

3C12G			THREE CONDUCTORS,#12 AWG, STRANDED, 600V INSULATION:

MATERIAL PVC,SHIELDED JACKETING: MATERIAL PVC, NOMINAL

O.D. (IN.) 0.395 ANIXTER PART # 2A-1203S

3C12OTN		THREE CONDUCTORS #12 AWG 19 STRAND, BARE COPPER, 600V,

90C XLPE JACKET LSNH, OVERALL SHIELD W/DRAIN, TRAY RATED.

LAKE CABLE VHX123S(19) O.D. 0.42"

3C12STOW		THREE CONDUCTORS, PVC JACKET AND INSULATION TYPE STOW, 600V,

#12 AWG,FLEXIBLE STRANDED COPPER WIRE, COLEMAN CABLE

P/N 20038 NOT FOR CABLE TRAY USE

3C12TYR		THREE CONDUCTORS, TYREX TYPE SO, 600V, #12 AWG,				1C		LFY,LRY#6,LRY#10

STRANDED, COPPER WIRE, 0.635" O.D. SLAC SN61-329-722-32

NOT FOR CABLE TRAY USE

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

3C12T3V		THREE CONDUCTORS, #12AWG, UNSHIELDED, 300V, PVC				1L		JAE4P, S&T

JACKET, CL-2 RATED ALPHA CAT # 1892/3C, 0.32" O.D. COLOR

CODE IS BLACK, RED AND WHITE.

3C12T6V		THREE CONDUCTORS, #12AWG, 600V, 0.381" O.D.,

PVC JACKET. ANIXTER CAT#2A-1203.

3C14FLX		THREE CONDUCTORS, #14AWG, 600V, SOLID COPPER,				1C		ACP, ACR

GROUND WIRE,TRAY CABLE, FLEXIBLE SHEATH, MFR. AMERICAN

FLEXIBLE CONDUIT CO. #14/2MC, 0.50" O.D.

3C14IW		THREE CONDUCTORS, #14AWG, INDIVIDUAL WIRE.

3C16FLX		THREE CONDUCTORS, #16AWG, COPPER. MFR: AMERICAN FLEX.

3C16T3V		THREE CONDUCTORS, 300V, #16AWG, STRANDED, TINNED			1L		LFB, MS5S

COPPER WIRE,TRAY CABLE, UNSHIELDED, PVC JACKET, 0.28"					MS8S,ACP,

O.D., ALPHA P/N 45073										ACJBX, LSB#8

3C16OS		THREE CONDUCTOR, #16 AWG, STRANDED, OVERALL SHIELD, 600V,		1N		S&T

TRAY CABLE PVC JACKET, 0.40" O.D., ALPHA CAT. #45440/3.

3C16TYR		THREE CONDUCTORS, TYREX TYPE SO, 600V, #16 AWG,				1C		LFB,LSB#6

STRANDED, COPPER WIRE, 0.43" O.D., SLAC SN 61-329-722-12.				ACP, ACJBX,

NOT FOR CABLE TRAY USE										ACR, LSR#6

3C18OS		THREE CONDUCTOR, #18 AWG, THERMOPLASTIC RUBBER JACKET,		1L		LFR, LSR#8

300V OVERALL SHIELDED, TRAY CABLE, 0.256" O.D., ALPHA

CAT. #45383.

3C18TLN		THREE CONDUCTORS, 18 AWG OVERALL SHIELD, LOW SMOKE ZERO

HALOGEN,TRAY CABLE CONDUCTOR 14 AWG AND SMALLER-TIN COATED

COPPER PER ASTM B286.

• CROSS-LINKED POLYETHYLENE (XLPE)

• COLOR CODE: METHOD 3 SHIELD:

• BRAIDED TIN-COATED COPPER JACKET

• LOW-SMOKE, ZERO-HALOGEN CROSS-LINKED

POLYOLEFIN (LSZH XL POLYO) BLACK (BLK) OR WHITE (WHT)

CABLES ARE MULTI-CONDUCTOR,

SHIELDED CONSTRUCTIONS, SUITABLE FORN NON-WATERTIGHT,

NON-FLEXING SERVICE.

• MILITARY P/N M24643/43-12UO, TYPE LS3SJ-18,O.D.=0.308

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

3C18TYR		THREE CONDUCTOR, #18 AWG, TYREX TYPE SO, 600V, 				1C		MS3S-S, LFR

STRANDED WIRE & CABLE CAT.#-703-4, 0.405" O.D. NOT

FOR CABLE TRAY USE.

3C20OS		THREE CONDUCTOR, #20 AWG, 300V, OVERALL SHIELDED, CM			1U

RATED, 0.218" O.D., BELDEN CAT. #8772.

3C20T3V		THREE CONDUCTORS, 300V, #20 AWG, STRANDED, TINNED-			1L		LFR, MS3S

COPPER WIRE, TRAY CABLE , UNSHIELDED, PVC JACKET, 0.22"

O.D., ALPHA CAT.#45053.

3C22OS		THREE CONDUCTORS, #22 AWG, STRANDED, OVERALL SHIELD,			1N

300V, THERMOPLASTIC RUBBER JACKET, TRAY CABLE, 0.22"

O.D., ALPHA CAT.#45193.

3PR16OS		THREE PAIR, #16 AWG, STRANDED, TRAY CABLE, OVERALL			1F		MS5P, MS5S

SHIELD, 300V 0.36" O.D., BELDEN CAT. #1528A.

3PR18OS		THREE PAIRS, #18 AWG, 300V TRAY CABLE, OVERALL				1F		LFR, MS6S

SHIELDED, STRANDED TINNED COPPER O.42" O.D., BELDEN

CAT.#9553.

3PR20IS		THREE PAIRS, DIGITAL DATA TRANSMISSION CABLE, #20			1D		ST4, ST5, ST6

AWG, STRANDED, TINNED-COPPER WIRE, INDIVIDUALLY SHIELDED				MS6P, MS6S

PAIRS, WITH ONE ISOLATED DRAIN WIRE FOR EACH PAIR.

0.64" O.D., 110 OHMS, BELDEN SPECIAL.

3PR20OS		THREE PAIRS, #20 AWG, STRANDED, COPPER WIRE,

OVERALL SHIELDED, TRAY CABLE, 300V, 0.31" O.D., ALPHA

CAT. #45453.

3PR22IS		THREE PAIRS, AUDIO AND DATA TRANSMISSION CABLE, #22			1D

AWG, STRANDED, CM RATED, TINNED-COPPER WIRE,

INDIVIDUALLY SHIELDED PAIRS, WITH ONE ISOLATED DRAIN WIRE

FOR EACH PAIR, PVC JACKET, 0.3" O.D., BELDEN CAT. #8777.

3PR22ISH		3PR #22AWG, STRANDED COPPER WIRE, INDIVIDUALLY SHIELDED,

TEFLON INSULATED, WITH 1 ISOLATED DRAIN WIRE PER PAIR,

CHROME PVC JACKET, 300 VOLT, CM RATED, 0.345" O.D.,

'DATALINE' CONTROLLED IMPEDANCE CABLE BELDEN CAT#82777.

3PR22OS		THREE PAIRS, #22 AWG, STRANDED, COPPER WIRE,				1F		LFR, LFB

OVERALL SHIELDED, TRAY CABLE, 300V, 0.326" O.D., BELDEN				MS6PB, MS6PA

CAT. #9513.												MS8S, MS10S

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

3PR24CB		THREE TWISTED PAIRS, #24 AWG STRANDED TINNED COPPER

DRAIN WIRE, FEP TEFLON INSULATED, OVERALL BELDFOIL

ALUMINUM-POLYESTER SHIELD, 300V RMS, 0.241 O.D.,

BELDEN CAT.#88103.

3PR24IS		3 PAIR, #24 AWG, STRANDED, COPPER WIRE, INDIVIDUALLY			1P		MS6PSB, TT8P

SHIELDED, WITH 1 ISOLATED DRAIN WIRE PER PAIR, CHROME PVC				DAY-20, TT8PR

JACKET, 300 VOLT, CM RATED 0.345" O.D., 'DATALENE					TT12P, MS6P

CONTROLLED IMPEDANCE CABLE, BELDEN CAT. #9730 						DB15P

SLAC SN 61-329-200-03.

3PR24OS		THREE PAIRS, #24 AWG, 300V, OVERALL SHIELDED,				1H		LFR, BSR

STRANDED TINNED COPPER, TWISTED PAIRS, 0.27" O.D., TRAY

CABLE, ALPHA CAT. #45493.

3PR24PLN		THREE PAIR #24 AWG. PLENUM CABLE NEC 725, BARE

COPPER CONDUCTORS WITH TINNED DRAIN. 0.167" O.D.

MFG. ALPHA P/N#57603.

3PR28OS		THREE PAIR, #28 AWG, STRANDED TINNED COPPER WIRE,

OVERALL SHIELD, TRAY CABLE, 0.260" O.D., BELDEN CAT. #8133.

3TT22OS		COMPUTER CABLE,3 CONDUCTORS,22AWG GAUGE,300V,80DEGC

TEMPERATURE	CHROME COLOR, S-R PVC INSULATION,30AWG,

7 STRANDING, 0.202 IN. OUTER DIAMETER, POWER ELECTRONIC

CABLE TYPE. BELDEN #9939 3C22OS(RS232)

350TLSNH		350KCMIL, 90DEG/105DEG. C, TC, LOW SMOKE NON-HALOGEN (LSNH),			LB35-9,LB35-10

600V.INSULATION COLOR GRAY, 0.990" O.D., WT= 1.3LB/FT,				LB35D9

AMERICAN PART # 39777. AMERICAN INSULATED WIRE CORP P/N 39780

(BLACK INSULATION).

373FLX		MINIMUM WIRES PER CONDUCTOR 925,NOMINAL INSULATION THICKNESS

IN 0.075, NOMINAL JACKET THICKNESS IN 0.065, NOMINAL OUTSIDE

DIAMETER IN 1.110, APPROX. WEIGHT LBS. PER 1,000 FT. 1436,

AMPACITY 90DEG. 591, EXTRA FLEXIBLE CABLE, 325 STRANDS, 600V,

0.65" O.D., PART # AMERCABLE 37-119-217 ID 1.110"

PLEASE SEE GENERAL NOTES # 8

4C2/0OS		FOUR CONDUCTORS, #2/0 AWG, TYPE MC(XHHW), 600V,						LB02-6, LB02DB

TRAY CABLE,1.32" O.D., ALUMINUM SHEATH.OKONITE CAT.#571-31-3289.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4C2AS			OKONITE C-L-X® TYPE MC-HL (XHHW-2) 600V POWER CABLE WITH

ALUMINUM SHEATH. FOUR COPPER CONDUCTORS/90°C WET OR DRY RATING

FOR CABLE TRAY USE. OKONITE PART NUMBER 571-31-3276.

4C2NS			OKONITE C-L-X® TYPE MC-HL (XHHW-2) 600V POWER CABLE

WITH-OUT ALUMINUM SHEATH FOUR COPPER CONDUCTORS/90°C WET

OR DRY RATING FOR CABLE TRAY USE.

OKONITE PART NUMBER 571-31-3276

4C6PVC		FOUR CONDUCTORS, #6 AWG, PVC JACKET AND INSULATION, 600V,

FLEXIBLE STRANDED COPPER WIRE. O.D. 0.986"

MFG: LAPPUSA, OLEFLEX 190. P/N: 600604.

NOT FOR CABLE TRAY USE

4C8AS			FOUR CONDUCTORS, #8 AWG, 600V, ALUMINUM SHEATH, TRAY			1B		LR8U10

CABLE, OKONITE CLX TYPE MC (XHHW), CAT-# 571-31-3264,

0.95" O.D.

4C8SHLD		OKONITE C-L-X® TYPE MC-HL (XHHW-2) 600V POWER CABLE WITH

ALUMINUM SHEATH FOUR COPPER CONDUCTORS/90°C WET OR DRY RATING

FOR CABLE TRAY USE.OKONITE PART NUMBER 571-31-3263

4C8T6V		FOUR CONDUCTORS, #8 AWG, STRANDED, PVC/NYLON PVC			1F

CONTROL CABLE, 0.658" O.D., TRAY CABLE, UNSHIELDED,

90 DEGREE C, 600V, ANIXTER CAT. #3G-0804.

4C8TYR		FOUR CONDUCTOR, TYREX TYPE SO, 600V, #8 AWG,				1A		LR8U10, ACP20

STRANDED, COPPER WIRE, 0.82" O.D., STANDARD WIRE &

CABLE CO. CAT. #705-15. NOT FOR CABLE TRAY USE.

4C10FST		FOUR CONDUCTOR, PVC FLAT FESTOON CABLE, 600V, #10 AWG.

4C10T6V		FOUR CONDUCTORS, #10AWG, STRANDED, TRAY CABLE,				1B		MS8PA, MS8SA

600V, 0.556" O.D., UNSHIELDED, ANIXTER CAT. #2MR-1004.				MS8PW, MS8PY, LRY#6R

4C10TYR		FOUR CONDUCTOR, TYREX TYPE SO, 600V, #10 AWG,				1A

STRANDED, COPPER WIRE, 0.745" O.D., STANDARD WIRE &

CABLE CO. CAT. #703-30. NOT FOR CABLE TRAY USE.

4C12OJ		4 CONDUCTORS, #12 STRANDED, OVERALL JACKET, UNSHIELDED

WIRES COLORED:BLACK, RED, BLUE, WHITE. SPECIAL CABLE FOR

LINAC CORRECTORS.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4C12PVC		FOUR CONDUCTORS, #12 AWG, PVC JACKET AND INSULATION, 600V,

FLEXIBLE STRANDED COPPER WIRE. O.D. 0.460"

MFG: LAPPUSA, OLEFLEX 190. P/N: 601204.

NOT FOR CABLE TRAY USE

4C12T6V		FOUR CONDUCTORS, #12AWG, STRANDED, TRAY CABLE,				1B		MS8PA, MS8SA

600V, 0.468" O.D., UNSHIELDED, ANIXTER CAT.#2MR-1204.					MS8PW, MS8PY, LRY#6R

4C12TYR		FOUR CONDUCTOR, #12 AWG, TYREX TYPE SO, 600V,				1A		LRY#10

STRANDED, COPPER WIRE, 0.665 O.D., STANDARD WIRE &

CABLE CO. CAT. #703-24. NOT FOR CABLE TRAY USE.

4C14IW		FOUR CONDUCTORS, #14AWG, INDIVIDUAL WIRE.

4C16FLX		FOUR CONDUCTORS, #16 AWG, 600V, SOLID COPPER,				1Q

GROUND WIRE, TRAY CABLE, FLEXIBLE SHEATH, MFR. AMERICAN

FLEXIBLE CONDUIT CO., 0.5" O.D.

4C16OS		FOUR CONDUCTORS, #16 AWG, STRANDED, COPPER WIRE,OVERALL		1L

SHIELD, TRAY CABLE, 300V, 0.31" O.D., ALPHA NO. #45364.

4C16PLEN		FOUR CONDUCTORS, #16 AWG, PLENUM CABLE, TINNED COPPER			2

CONDUCTORS, TEFLON INSULATED, BELDFOIL ALUMINUM-

POLYESTER SHIELD WITH 85% TINNED COPPER BRAID SHIELD.

TEFLON JACKET. NEC 800. 0.228"O.D., BELDEN P/N 83704.

4C16S/U		FOUR CONDUCTOR, #16 AWG, TWO CONDUCTORS ARE						LFB & BULLET

INDIVIDUALLY SHIELDED AND THE OTHER TWO CONDUCTORS ARE

NOT SHIELDED, 0.5" O.D.

4C16T3V		FOUR CONDUCTOR, #16 AWG, TRAY CABLE, 300V,				1L		LFB

STRANDED TINNED COPPER WIRE, UNSHIELDED, 0.44" O.D.,

ALPHA CAT. #45074.

4C16T6V		FOUR CONDUCTORS, #16AWG, TRAY CABLE, UNSHIELDED.

4C16TYR		FOUR CONDUCTORS, TYREX TYPE SO, 600V, #16 AWG,				1A

STRANDED, COPPER WIRE, 0.485" O.D., STANDARD WIRE &

CABLE CO.CAT. #703-12. NOT FOR CABLE TRAY USE.

4C18OS		FOUR CONDUCTORS, #18 AWG, STRANDED, COPPER WIRE,			1L		BULLET

OVERALL SHIELD, TRAY CABLE, 300V, 0.27" O.D., ALPHA NO.

#45384.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4C18TEF		FOUR CONDUCTORS, #18 AWG, TINNED COPPER, TEFLON

INSULATED, OVERALL TAPE WRAP, 0.167 O.D., BELDEN CAT.#88489.

4C20OS		FOUR CONDUCTORS, #20 AWG, STRANDED, COPPER WIRE,			1L		LFR, TT4S

OVERALL SHIELD, TRAY CABLE, 300V, 0.25" O.D., ALPHA NO.				DAY20, MS10PA

#45464.

4C20OTN		FOUR CONDUCTORS, 20 AWG, SHIELDED, LOW SMOKE ZERO HALOGEN,

300V, TRAY CABLE, O.D. 0.234 IN., LAKE CABLE P/N: TXH204S.

4C22			FOUR CONDUCTORS ENCASED IN RADIATION RESISTANT SPIRAL WRAP.

THE SPIRAL WRAP IS SPLIT LOOM TUBING, 0.25" O.D. METRA

PART#14. METRA - (800)271-0932, EXT. 249, SALES.

4C22OS		FOUR CONDUCTORS, #22AWG, 300V, TINNED COPPER, 2 SHIELDED

AND 2 UNSHIELDED CONDUCTORS. 0.165" O.D. BELDEN#8724.

4C22T6V		FOUR CONDUCTORS, #22AWG, TRAY CABLE, 600V, STRANDED TINNED

COPPER WIRE, UNSHIELDED, 0.295" O.D.

4MTW-B		ONE CONDUCTOR, #4AWG, STRANDED, WIRE TYPE MTW, BLACK,

TFF, AWM, TEW, 600V, 500 FEET SPOOL.

4PR16AS		FOUR PAIRS, ARMORED CABLE, 300V, #16 AWG, STRANDED,			1F		LFB, LFB-B,

TRAY CABLE TINNED COPPER WIRE, OVERALL SHIELD AND DRAIN				LSB-G, WNY,

WIRE, O.82"O.D., OKONITE CLX TYPE P-OS 561-10-3404.					LSB#6, LRB#10

4PR16IS		FOUR PAIR, #16 AWG, INDIVIDUALLY SHIELDED, 600 VOLT,

TRAY CABLE 0.578" O.D., BELDEN CAT. #1039A.				1F

4PR16OS		FOUR PAIR, #16 AWG, 600V, 0.558" O.D., OVERALL				1F		LRB#6, HR13S

SHIELD,TRAY CABLE BELDEN CAT. #1070A.

4PR16TC		FOUR PAIR, #16AWG, 600V, OVERALL SHIELDED. MFR: OKONITE.

4PR16TLN		FOUR PAIR, #16 AWG, 600 VOLT INDIVIDUALLY SHIELDED,

LOW SMOKE NON HALOGEN, TRAY CABLE, 0.610 O.D.,

LAKE CABLE # VXH164SPOS.

4PR16XS		FOUR PAIR, #16 AWG, INDIVIDUALLY SHIELDED, OVERALL SHIELD,

300 VOLT, TRAY CABLE, LSZH, OD: 0.451 in. 166 Lbs/Mft.

USE Lake Cable P/N: TXH164SPOS.

4PR18AS		FOUR PAIR ARMORED CABLE, 300V, #18 AWG, STRANDED			1F

TINNED COPPER WIRE, OVERALL SHIELD WITH DRAIN WIRE, TRAY

CABLE, 0.82" O.D., OKONITE CLX TYPE SP-OS, OKONITE CAT

#561-10-3304.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4PR18ITN		FOUR PAIR, # 18 AWG, INDIVIDUALY SHIELDED PAIRS WITH DRAIN

WIRE, BLACK AND WHITE NUMBERED PAIRS, TRAY CABLE, LOW SMOKE

ZERO HALOGEN, SUNLIGHT RESISTANT, OVERALL ALUM MYLAR SHIELDED.

0.418" O.D. MFG: LAKE CABLE, P/N: TXH184EPS.

4PR18OS		FOUR PAIR, #18 AWG, 300V, OVERALL SHIELD, STRANDED			1F

TINNED COPPER, TRAY CABLE, BELDEN CAT. #9554. 0.458" O.D.

4PR18OTN		FOUR PAIR, # 18 AWG, 19 STRAND BARE COPPER WIRE. FLAME

RETARDANT CROSS LINKED PE INSULATION, OVERALL ALUM MYLAR

SHIELD, 18 AWG 7 STRAND TC DRAIN WIRE, BLACK ZERO HALOGEN

POLYOLEFIN JACKET. TYPE ITC. CABLES ALSO MEETS THE

REQUIREMENTS OF UL STANDARD 1685 FOR LIMITED SMOKE (UL)

LSZH LS LIST.0.415” O.D. LAKE CABLE P/N TXH184PRS(19).

4PR18TC		FOUR PAIR, #18AWG, TRAY CABLE.

4PR18XS		FOUR PAIRS, #18AWG, INDIVIDUAL SHIELDED, OVERALL SHIELD,

LSZH, 300 VOLT, OD: 0.410 inches. 127 Lbs/Mft Lake Cable P/N: TXH184SPOS.

4PR20IS		FOUR PAIR, #20 AWG, INDIVIDUALLY SHIELDED, STRANDED			1F

TINNED COPPER, CL2 RATED, 30V, ETHERNET CABLE, 0.36"

O.D., BELDEN CAT.#9892.

4PR20OS		FOUR PAIR, #20 AWG, OVERALL SHIELDED, STRANDED				1F

TINNED COPPER, TRAY CABLE, 300V, 0.412" O.D., BELDEN CAT.

#1056A. WT= 0.097 LB/FT

4PR20XS		FOUR PAIR, #20 AWG, INDIVIDUALLY SHIELDED, OVERALL SHIELD,

STRANDED, 300 VOLT, LSZH, OD: 0.402 inches. 103 Lbs/Mft.

Lake Cable P/N: TXH204SPOS

4PR22IS		FOUR PAIR, #22AWG, STRANDED TINNED COPPER,				1F

INDIVIDUALLY SHIELDED, TRAY CABLE, 300V, 0.360" O.D.,

BELDEN CAT. #9330.

4PR22ITN		FOUR PAIR, #22AWG, STRANDED TINNED COPPER, INDIVIDUALLY

SHIELDED, LOW SMOKE ZERO HALOGEN, 300V PLTC. 0.347” O.D.

WT=.074 LBS/FT. LAKE P/N 050731 SWC3.

4PR22OS		FOUR PAIR #22 AWG, STRANDED TINNED COPPER WIRE,				1F		LFR, TT8P

OVERALL SHIELD, 300V, TRAY CABLE, 0.353" O.D. BELDEN CAT#9514.			AMP8P, AMP8S

4PR24CC		FOUR TWISTED PAIRS, #24AWG, TINNED COPPER, INDIVIDUALLY

SHIELDED, CHROME PVC JACKET. 0.388" O.D. BELDEN#8164.

4PR24FRP		FOUR PAIR, #24AWG, TINNED COPPER, FOAMED TEFLON						AMP9F

INSULATED, TWISTED PAIRS, GRAY FLUOROCOPOLYMER JACKET,

300V RMS, 0.261"O.D. BELDEN CAT#88104.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4PR24IS		FOUR PAIR, #24AWG, STRANDED COPPER WIRE,					1P		TT8P

INDIVIDUALLY SHIELDED, 300 VOLT, CM RATED, 0.363" O.D.,

BELDEN CAT. #9728, "DATALENE" CONTROLLED IMPEDANCE CABLE.

4PR24ITN		FOUR PAIR, 24AWG, STRANDED COPPER WIRE,

INDIVIDUALLY SHIELDED, 300 VOLT,

0-HAL BLK JACKET, CM RATED, 0.375" O.D.,

4PR24NS		FOUR PAIR, #24AWG, NO SHIELD. BELDEN CAT3, PVC JACKET,

TELEPHONE WIRE.

4PR24OS		FOUR PAIR, #24AWG, STRANDED COPPER WIRE, OVERALL

SHIELD, TRAY CABLE, 0.388" O.D., BELDEN CAT. #8164.

4PR350		FOUR PAIR TWISTED UNSHIELDED, #24 AWG, SOLID BARE COPPER,

FEP PVC INSULATED, CATEGORY 5, TRAY RATED, 0.188" O.D.,

350MHZ ETHERNET CABLE.

4PR350PLN		FOUR PAIR TWISTED UNSHIELDED, #24 AWG, SOLID BARE

COPPER, FEP TEFLON INSULATED, CATEGORY 5, TRAY RATED,

0.188" O.D., 350MHZ ETHERNET CABLE.

4-PACK		FOUR COAXIAL CABLES INSIDE A SINGLE JACKET WITH

CONNECTORS INSTALLED. THIS CABLE ASSEMBLY IS SUPPLIED BY

DESY FOR THE FFTB WPM'S. 0.6" O.D.						NA

4PRCAT3		FOUR PAIR,#24AWG, PLENUM OR PVC CABLE, CATEGORY 3.

TELEPHONE CABLE.

4PRCAT5		FOUR PAIR, #24AWG, PLENUM CABLE, CATEGORY 5. DATA CABLES.

4PRPLEN		FOUR PAIR, #24 AWG, SOLID BARE COPPER, FEP TEFLON			1b

INSULATION, CMP RATED, UNSHIELDED, PLENUM CABLE,

0.200" O.D., CATEGORY 5. BELDEN CAT. #1585A,YM28822.

4PRPLEN2		FOUR PAIR, #24AWG, 350mhz, BELDEN CAT#1585A.

4PRPVC		FOUR PAIR, #24 AWG, SOLID BARE COPPER, PVC				1b

INSULATION, CMP RATED, UNSHIELDED CABLE, 0.217" O.D.,

CATEGORY 5. BELDEN CAT. #1583A, YM2881.

4PRPVC1		FOUR PAIRS, #24 AWG, WHITE, PVC JACKET, SOLID BARE

COPPER, UNSHIELDED, 0.217" O.D., CATEGORY 5, BELDEN

CAT. #1701A.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

4SMMTLN		4-STRAND, 50/125UM, (550 METER 10-GBE), MULTI-MODE,

OPTICAL BREAKOUT CABLE.  LOW-SMOKE, ZERO-HALOGEN CABLE

SUITABLE FOR TRAYS AND RISERS. AQUA OUTER JACKET.

OUTER DIAMETER: 9.1MM(.36").  SUB-CABLE DIAMETER: 2.5MM(.10").

MINIMUM INSTALLATION BEND RADIUS: 13.6CM(5.4").

MINIMUM LONG-TERM BEND RADIUS: 9.1CM(3.6").

OPTICAL CABLE CORPORATION PART NUMBER: BX004ZALE9QZ

4SSMTLN		4-STRAND, 9/125UM, SINGLE-MODE, OPTICAL BREAKOUT CABLE.

LOW-SMOKE, ZERO-HALOGEN CABLE SUITABLE FOR TRAYS AND RISERS.

YELLOW OUTER JACKET. OUTER DIAMETER: 9.1MM(.36").

SUB-CABLE DIAMETER: 2.5MM(.10"). MINIMUM INSTALLATION

BEND RADIUS: 13.6CM(5.4").  MINIMUM LONG-TERM BEND RADIUS: 9.1CM(3.6").

OPTICAL CABLE CORPORATION PART NUMBER: BX004ZSLB9YZ

4THHN			ONE CONDUCTOR, #4AWG, 7 STRAND,600V, SLAC S/N61-328-370-01

5C4IW			FIVE CONDUCTOR, #4AWG,COPPER CONDUCTORS, 19 STRANDS

PER CONDUCTOR, 600V, 90 DEGREES, TRAY RATED, XLPE BLACK

INSULATION, UV RESISTANT.MANCO: PART # MA0504GCT

5C4LSNH		NUMBER & CIRCUIT CONDUCTOR SIZE 5C/#4 AWG, AVERAGE

INSULATION THICKNESS 45 MILS, AVERAGE JACKET THICKNESS

80 MILS, NOMINAL CABLE O.D. 1.090 IN, NOMINAL CABLE WEIGHT

1011 LBS/1000 FT. MULTI-CONDUCTOR, 600V,HEAT, MOISTURE AND

SUNLIGHT RESISTANT, BLACK, POLYOLEFIN OR EQUIVALENT

LOW SMOKE ZERO HALOGENATED INSULATING MATERIAL, WET OR DRY

LOCATION AT 90 DEGREES C. PART # DRAKA 400288

5C8SO			FIVE CONDUCTORS, #8 AWG, TYPE SO/SOOW, 0.90” O.D.,600V,

SUPPLIER: ANIXTER, P/N: 4A-0805.

5C8TYR		PORTABLE POWER CABLE, ALPHA TYPE G, 4 CONDUCTOR WITH GROUND,

ALPHA PART NUMBER 7760 OR EQUIVALENT, 2KV, 45A, #8 AWG

NOT FOR CABLE TRAY USE.

5C10PVC		FIVE CONDUCTORS, PVC JACKET AND INSULATION, 600V, #10 AWG,

FLEXIBLE STRANDED COPPER WIRE, LAPPUSA OLEFLEX 190

P/N 601005 NOT FOR CABLE TRAY USE

5C10SO6V		FIVE COPPER CONDUCTOR #10AWG, TYPE SO, STRANDED (105 STRANDS), 			LRY#10

SYNTHETIC RUBBER INSULATED, THERMOSET JACKETTED, 90 DEGREES

"C", 600V, 0.79 O.D., ANIXTER CAT # 4A-1005.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

5C10TYR		FIVE CONDUCTORS, #10AWG, TYREX. SLAC S/N61-329-722-44

5C10T6V		FIVE CONDUCTOR, #10 AWG, 600V, UNSHIELDED, TRAY

CABLE, 0.615: O.D., ANIXTER CAT. #2MR-1005.

5C12TYR		FIVE CONDUCTORS, #12 AWG, 600V, TYREX TYPE SO,						LFY, LRY#8

STRANDED COPPER WIRE,NEOPRENE,105 DEGREE C RATED,

0.71" O.D., SLAC S/N 61-329-722-34. NOT FOR CABLE TRAY USE.

5C14IW		FIVE CONDUCTORS, #14AWG, INDIVIDUAL WIRE.

5C16OS		FIVE CONDUCTORS, #16 GAUGE, STRANDED, OVERALL FOIL			1N		MS5S, TT4S

SHIELD, 600 V, TRAY CABLE, 0.48" O.D., ALPHA CAT. #45440/5.

5C16T6V		FIVE CONDUCTORS, #16 AWG, 600 VOLT, TRAY CABLE,				1N		LFB, LFR

STRANDED, UNSHIELDED, O.47" O.D., ALPHA P/N 45435.					MS11S, LSB#6

5C16TYR		FIVE CONDUCTORS, TYREX TYPE SO, 600V, #16 AWG,

STRANDED TRAY CABLE, SLAC S/N61-329-722-14.NOT FOR CABLE

TRAY USE.

5C18TC		FIVE CONDUCTORS, #18AWG, 300V, STRANDED TINNED

COPPER CONDUCTORS, PVC JACKET. 0.26" O.D. ALPHA#1898/5.

5C18T6V		FIVE CONDUCTOR, #18 AWG, STRANDED, TRAY CABLE,				1N		LFR, MS8P

600V, UNSHIELDED, ALPHA CAT. #45425, 0.44" O.D.

5C20OS		FIVE CONDUCTOR, #20AWG, STRANDED, OVERALL SHIELD, 600V,		1N		LFR

TRAY CABLE, 0.42" O.D., ALPHA CAT. #45420/5.

5PR20OS		FIVE PAIR, #20 AWG, 300 VOLT, OVERALL SHIELD, TRAY

CABLE, 0.38" O.D., ALPHA CAT. #45455. IF EITHER END IS A

VAT7S CONNECTOR, BOTH ENDS ARE COLOR CODE: >>				1R,1H		VAT7S, MS8S

5PR22ITN		FIVE PAIR, #22 AWG, 7STR BARE COPPER WIRE WITH .021"

LSXLPE INSULATION, INDIVIDUAL SHIELDED WITH DRAIN WIRE,

300V, LOW SMOKE ZERO HALOGEN, TRAY CABLE, 0.471" O.D.,

BLK & WHT NUMBERED PAIRS. MFG: LAKE CABLE, P/N:TXH225EPS.

5PR22OS		FIVE PAIRS, #22 AWG, 300V, TRAY CABLE, OVERALL				1H

SHIELDED, 0.30" O.D., ALPHA NO. 45495.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

5PR24CB		FIVE PAIRS, #24AWG, TINNED COPPER, FEP TEFLON

INSULATION, GRAY FLUOROCOPOLYMER JACKET, 300V RMS,

0.269" O.D. BELDEN CAT#88105.

5PR24OS		FIVE TWISTED PAIRS, #24AWG STRANDED TINNED COPPER

DRAIN WIRE, OVERALL BELDFOIL ALUMINUM-POLYESTER SHIELD,

FEP TEFLON INSULATED, FLAME ARREST JACKET, 0.196" O.D.,

BELDEN CAT.#82505.

5PR28F		FIVE TWISTED PAIR, #28 AWG, TWIST'N'FLAT CABLE, LAMINATED				DB9S

T'N'F, STYLE 2697, 300V, AMPHENOL SPECTRA-STRIP P/N

843-132-2801-010

5PR28OS		FIVE TWISTED PAIR, #28AWG, OVERALL SHIELD.

TINNED COPPER, CHROME PVC JACKET. 0.300" O.D.

BELDEN CAT#8135.

500TLSNH		500KCMIL,FLEX, 90DEG/105DEG. C, TC, LOW SMOKE NON-HALOGEN,				LB60D8, LB60-8

(LSNH)600V. INSULATION COLOR GRAY, 1.150" O.D.,WT=1.775LB/FT			LB60S8, 500MSCI

AMERICAN P/N39778.AMERICAN INSULATED WIRE CORP P/N39914

(BLACK INSULATION)

6C14IW		SIX CONDUCTORS, #14AWG, INDIVIDUAL WIRE.

6C16OS		SIX CONDUCTORS, #16AWG, 300V, OVERALL SHIELDED,

0.35" O.D. ALPHA CAT#5366.

6C18TC		SIX CONDUCTORS, #18AWG, 300V, STRANDED TINNED

COPPER, TRAY CABLE, UNSHIELDED. PVC JACKET. 0.29" O.D.

ALPHA CAT#1898/6.

6C20OTN		SIX CONDUCTORS, 20 AWG, SHIELDED, LOW SMOKE ZERO

HALOGEN, 300V, TRAY CABLE, O.D. 0.283 IN.,

LAKE CABLE P/N: TXH206S.

6C26MLC		SIX CONDUCTORS, #26AWG, STRANDED FLAT MODULAR LINE CORD,

SPC TECHNOLOGY TYPE#8588-0182 STOCK #52N9472.

6PR16ITN		SIX INDIVIDUALLY SHIELDED PAIRS,#16AWG,600VOLT,UL

LISTED LSZH Type XLPE UL STANDARD 66,1277,1581,

NEC Type TC - TRAY RATED CABLE. LAKE CABLE

P/N VXH166EPS/20DR. .720 OD,266lb per 1000ft.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

6PR16OS		SIX PAIRS, #16 AWG, OVERALL SHIELD, 600 VOLT, TRAY

CABLE, 0.660" O.D., ANIXTER CAT. #2AS-1606POS.

6PR18IS		SIX PAIRS, #18 AWG, INDIVIDUALLY SHIELDED. BELDEN

CAT#9774. NEWARK 36F1395WA.

6PR18OS		SIX PAIRS, #18 AWG, OVERALL SHIELDED, 300V, TRAY			1F

CABLE, 0.481" O.D., BELDEN CAT. #9556.

6PR18T3V		SIX PAIR, #18 AWG, 300V, TRAY CABLE, UNSHIELDED,			1H

0.45" O.D., ALPHA CAT. #45036.

6PR20IS		SIX PAIR #20 AWG, 30V, INDIVIDUALLY SHIELDED,.427" O.D.

CM TYPE, COLOR CODE CHART NO. 3. ANIXTER/BELDEN CAT.# 9874

6PR20T3V		SIX PAIR, #20 AWG, 300V, TRAY CABLE, UNSHIELDED,			1H

0.40"O.D., ALPHA CAT. #45286.

6PR22ITN		SIX PAIR, #22 AWG, INDIVIDUAL SHIELDED WITH DRAIN WIRE,

300V, LOW SMOKE ZERO HALOGEN, TRAY CABLE, 0.471" O.D.,

MFG: LAKE CABLE, P/N: TXH226EPS.

6PR22IS		SIX PAIR, #22 AWG, INDIVIDUAL SHIELDED, 300V, TRAY			1D

CABLE,0.437: O.D., BELDEN CAT. #9331.

6PR22OS		SIX PAIR, #22 AWG, STRANDED, OVERALL SHIELDED, 300			1F		LFR, MS8P

VOLT, TRAY CABLE 0.425" O.D., BELDEN CAT. #9516.					TT12S, DB-PS

6PR22OTN		LAKE CABLE TXH226PRS 22 AWG 6 PAIR 7 STRAND BARE COPPER WIRE,

XLPE INSULATION. SHIELDED WITH AN OVERALL LSZH JACKET, 300VOLT, TRAY RATED.

6PR24IS		SIX PAIR, #24 AWG, STRANDED, COPPER WIRE,					1P		AMP24P

INDIVIDUALLY SHIELDED, CM RATED 0.421" O.D.,ISOLATED

DRAIN WIRE PER PAIR, CHROME PVC JACKET, 300V, BELDEN CAT.

#9731, 'DATALENE' CONTROLLED IMPEDANCE CABLE.

6PR24OS		SIX PAIR, #24 AWG, OVERALL SHIELD, TINNED COPPER,

S-R PVC INSULATED WITH OVERALL BELDFOIL SHIELD, PLUS

65% TINNED COPPER BRAID SHIELD, CHROME PVC JACKET,

0.311" O.D., MFG BELDEN, P/N #8336.

7C12T6V		SEVEN CONDUCTORS, #12AWG, 600V, 0.495" O.D., PVC JACKET.

MFR: ANIXTER.

7C18TC		SEVEN CONDUCTORS, #18AWG, 300V, STRANDED TINNED COPPER,

UNSHIELDED TRAY CABLE. PVC JACKET. 0.29" O.D.

ALPHA CAT#1898/7.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

7C18T6V		SEVEN CONDUCTORS, #18 AWG, STRANDED, TRAY CABLE,			1N		LFR, TT12S

600V, 0.46" O.D., UNSHIELDED, ALPHA CAT. 45427.

7C22OS		SEVEN CONDUCTORS, #22 AWG, OVERALL SHIELD, 0.308" O.D.,		1W		TT4P

300V, SLAC PURCHASE SPECIFICATION #PS-114-001-03-R2.

7PR24IS		SEVEN PAIR, #24AWG, 150V, STRANDED, TINNED COPPER

WIRE, INDIVIDUALLY SHIELDED, PLENUM RATED, NEC CMP,

0.367" O.D., BELDEN CAT #89757.

7PR22OSS		SLAC MADE, 7 TWISTED PAIRS OF 22 AWG, TINNED

STRANDED COPPER. WIRES ARE TFE INSULATED (RED/WHITE).

WIRES ARE THEN WRAPPED IN STRANDED,TINNED COPPER

EXPANDABLE WIRE TUBES

(.38 DIAMETER TYP.- MIL-SPEC INC P/N 2146)AND

THEN WRAPPED IN STRANDED EXPANDABLE POLYETHYLENE TUBES

(ALTA TECH, 1" DIA PE FLEXIBLE TUBE).

8C10T6V		EIGHT CONDUCTORS, #10 AWG, STRANDED, TRAY CABLE,			1B

0.682"O.D. UNSHIELDED, 600V, ANIXTER CAT. #2A-1008.

8C12TLN		EIGHT CONDUCTORS, 12AWG TC 600V 90C BARE COPPER WIRE,

FLAME RETARDANT PE INSULATION,NON-SHIELDED. BLACK

ZERO-HALOGEN POLYOLEFIN JACKET. CABLE MEETS REQUIREMENTS

OF UL STANDARD 1685 FOR LIMITED LOW SMOKE. UL LS LISTED.

LAKE CABLE P/N 03602WGP2. 0.72" O.D.

8C12T6V		EIGHT CONDUCTORS, TRAY CABLE, 600V, #12 AWG,				1B		MS8PA,MS8PW

UNSHIELDED, 0.66" O.D., ANIXTER CAT. #2A-1208.						MS8PY, MS8SA,STRIP

8C14IW		EIGHT CONDUCTORS, #14AWG, INDIVIDUAL WIRE.

8C16/3V		EIGHT CONDUCTORS, #16AWG, 300V, STRANDED TIN

COATED COPPER, UNSHIELDED. 0.41" O.D. ALPHA CAT#5078.

8C16T6V		EIGHT CONDUCTORS, #16AWG, TYPE TC.

8C18OS		EIGHT CONDUCTORS, #18AWG, 300V, STRANDED TIN

COATED COPPER,OVERALL SHIELDED.0.38" O.D. ALPHA CAT#5168.

8C20OS		EIGHT CONDUCTORS, #20AWG, 300V, STRANDED TIN

COATED COPPER,OVERALL SHIELDED.0.31" O.D.ALPHA CAT#5468.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

8C22OS		EIGHT CONDUCTORS, #22AWG, STRANDED, 300V, OVERALL

SHIELDED. CHROME SILVER OUTER JACKET.SLAC S/N61-329-318-07.

8MTW-B		ONE CONDUCTOR, #8AWG, STRANDED, WIRE TYPE MTW, BLACK,

TFF, AWM, TEW, 600V, 500 FEET SPOOL.

8PR16AS		EIGHT PAIR, #16 AWG, ARMORED CABLE, 300V, OKONITE			1F

CAT.#564-01-3408.

8PR16IS		EIGHT PAIRS, #16 AWG, STRANDED, 300V, INDIVIDUALLY			1F

SHIELDED, TRAY CABLE, 0.687" O.D., BELDEN CAT.#1494A.

8PR16OS		EIGHT PAIRS, #16 AWG, STRANDED, OVERALL SHIELD, TRAY			1F		LFB

CABLE, 300 VOLT, 0.601" O.D., BELDEN CAT. #1485A.

8PR18AS		EIGHT PAIRS, ARMORED CABLE, #18 AWG, STRANDED				1F

TINNED COPPER, OVERALL SHIELD AND DRAIN WIRE, 300V, TYPE

P-OS,0.99" O.D., OKONITE CAT.#564-10-3308.

8PR18OS		EIGHT PAIRS, #18 AWG, OVERALL SHIELDED, TRAY CABLE,			1F

600V, 0.603" O.D., BELDEN CAT.#1065A.

8PR20IS		EIGHT PAIRS, #20 AWG, STRANDED, TRAY CABLE,				1F		MS19S

INDIVIDUALLY SHIELDED PAIRS, 300V, 0.54" O.D.,BELDEN

CAT. #1077A.

8PR20OS		EIGHT PAIRS, #20 AWG, STRANDED, TRAY CABLE, OVERALL

SHIELD, 300V, 0.56" O.D., ANIXTER P/N 323-231-2008.

8PR20XS		EIGHT PAIRS, #20 AWG, STRANDED, TRAY CABLE,

INDIVIDUALLY SHIELDED PAIRS, OVERALL SHIELD, 300V, LSZH,

OD: USE Lake Cable P/N: TXH208SPOS.

8PR22OS		EIGHT PAIRS, #22AWG, OVERALL SHIELDED.

8PR24TC		EIGHT PAIRS, #24AWG,TELE CBL, COPPER CONDUCTORS.

MFR: PREMIER.

8PR28F		EIGHT TWISTED PAIR, #28 AWG, TWIST'N'FLAT CABLE, LAMINATED				DB15S

T'N'F, STYLE 2697, 300V, AMPHENOL SPECTRA-STRIP P/N

843-132-2801-016.

8PR28OS		EIGHT TWISTED PAIR, #28AWG, OVERALL SHIELDED. TINNED

COPPER, CHROME PVC JACKET. 0.330" O.D. BELDEN CAT#8138.

8PRPHONE		EIGHT PAIRS, #24 AWG, TELEPHONE CABLE, UNSHIELDED,					PUSHON

PVC, SOLID COPPER CONDUCTORS, TYPE MPR/CMR, LEVEL 4,

CATEGORY 3, MFR. PREMIER.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

8THHN		   ONE CONDUCTOR, #8 AWG, THHN, BLACK, 19 STRAND, 600V.

SLAC S/N 61-328-368-01.

9C12T6V		NINE CONDUCTOR, #12 AWG, TRAY CABLE, 600V,				1B		LFY, MS8PA

UNSHIELDED, HOUSTON WIRE & CABLE CAT #H01428						MS8PW, MS8PY

0.615" O.D.												MS8SA

9C18J			NINE CONDUCTORS, #18AWG, UNSHIELDED.

9C18OS		NINE CONDUCTORS, #18 AWG, 600V, TRAY CABLE, 0.48"			1N		MS8S

O.D., ALPHA CAT. #45410/9.

9C18T6V		NINE CONDUCTORS, #18 STRANDED, UNSHIELDED,				1N		AMP9S, GP-CON

0.54" O.D., 600 VOLT RATED. USED FOR MAGNET MOVERS,					LFR, LSB#6

TRAY CABLE, ALPHA CAT.#45429.									VAT7S

9C20OTN		NINE CONDUCTORS, #20 AWG, SHIELDED, LOW SMOKE ZERO HALOGEN,

300V, TRAY CABLE, 0.327” O.D.

MFG: LAKE CABLE, P/N: TXH209S.

9C24OS		NINE CONDUCTORS, #24 AWG, STRANDED TINNED COPPER, CM

RATED, 0.244" O.D., BELDEN CAT. 49906(A).

9PR18OS		NINE PAIR, #18AWG, OVERALL SHIELDED. MFR: OKONITE.

9PR18OTN		LAKE CABLE TXH189PRS 18 AWG 9 PAIR 7 STRAND BARE COPPER WIRE,

XLPE INSULATION. SHIELDED WITH AN OVERALL LSZH JACKET, 300VOLT, TRAY RATED.

XLPE per UL Standard 13. Shield: Aluminum Mylar Tape - 100% cover,

Drain Wire: 18awg 7 strand tinned copper.

Diameter: .549"

Weight: 202 LBS/Mft.

9PR20OS		NINE PAIR, #20AWG, OVERALL SHIELDED. MFR: OKONITE.

9PR22OS		NINE PAIR, #22 AWG, OVERALL SHIELDED, 300V, TRAY			1F

CABLE, 0.488" O.D.,BELDEN CAT. #9520.

9PR24IS		NINE PAIR, #24 AWG, TINNED COPPER INDIVIDUALLY				1P

SHIELDED, CM RATED, 300V, 0.488" O.D. BELDEN CAT.#9732.

9PR24ISP		NINE PAIR, #24AWG, INDIVIDUALLY SHIELDED,

POLYPROPYLENE INSULATED, COLOR CHART NO.3, 0.368"

O.D., MFG. BELDEN. P/N #9992.

9PR24OS		NINE TWISTED PAIRS, #24 AWG STRANDED TINNED COPPER DRAIN

WIRE, BELDFOIL OVERALL ALUMINUM-POLYESTER SHIELD, TEFLON

INSULATED, 0.246" O.D., BELDEN CAT.#82509.

10C16T3V		TEN CONDUCTOR, #16 AWG, 300V, STRANDED, UNSHIELDED,			1L		LSB#6, MS10P

TRAY CABLE, 0.43" O.D., ALPHA P/N 45080.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

10C18T3V		TEN CONDUCTOR, #18 AWG STRANDED, 300V, O.37"				1L		SPADE LUGS

O.D., UNSHIELDED, TRAY CABLE, ALPHA CAT. #45070.

10C18OS		TEN CONDUCTORS, #18 AWG, 300V, OVERALL SHIELDED,			1L		MS10P, MS10S

STRANDED, TRAY CABLE ,0.38" O.D., ALPHA CAT. #45390.

10C20OTN		TEN CONDUCTORS (5 PAIR), #20 AWG, LOW SMOKE ZERO HALOGEN,

300V, - UNCOATED COPPER PER ASTM B174.

• CROSS-LINKED POLYETHYLENE (XLPE) INSULATION

• COLOR CODE: METHOD 3 JACKET

• LOW-SMOKE, ZERO-HALOGEN CROSS-LINKED

POLYOLEFIN (LSZH XL POLYO) WHITE (WHT) JACKETED CABLES

ARE MULTI-CONDUCTOR, SHIELDED CONSTRUCTIONS,

SUITABLE FOR NON-WATERTIGHT, FLEXING SERVICE.

• MILITARY P/N M24643/12-02UN, TYPE LSSTOP-5, O.D. = 0.590

10C22J		   TEN CONDUCTORS, #22 AWG,300V, .294" O.D.,

ALPHA WIRE P/N 1180C

10C22OS		TEN CONDUCTORS, #22 AWG, 300V, STRANDED, TRAY				1N		MS10P

CABLE, OVERALL SHIELDED, ALPHA CAT.#45199/10, 0.32" O.D.

10MTW-B		ONE CONDUCTOR, #10AWG, STRANDED, WIRE TYPE MTW, BLACK,

TFF, AWM, TEW, 600V, 500 FEET SPOOL.

10PRTHRM		TEN PAIR, #20 AWG, OVERALL SHIELD, SOLID WIRE, TYPE					W1

PLTC THERMOCOUPLE EXTENSION CABLE, ASA/ISA TYPE TX,

OKONITE CAT-# 284-20-4120, 0.56" O.D. COLOR CODE: BLUE

(COPPER +) AND RED (CONSTANTAN -).

10PR16AS		TEN PAIRS, 300V, #16AWG, OVERALL SHIELD, TYPE

PLTC ARMORED INSTRUMENTATION CABLE. 1.21" O.D.

OKONITE P/N 561-10-3410.

10PR20GS		10 TWISTED PAIR, 20 AWG, SHIELDED, WITH NON-HALOGENATED 				POS19PS

SHEATH. LAKE CABLE P/N 071019WGP3.

10PR20TN		TEN PAIR, 20 AWG, SHIELDED, LOW SMOKE ZERO HALOGEN, 300V,

TRAY CABLE, O.D., 0.539 IN., LAKE CABLE P/N: TXH2010PRS.

10PR22OS		TEN PAIRS, #22AWG, OVERALL SHIELD.

10THHN		   ONE CONDUCTOR, #10 AWG, STRANDING 19,THHN,600V.

SLAC S/N 61-328-367-01.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

11PR22OS		ELEVEN PAIRS, 300V, #22 AWG, STRANDED, TRAY CABLE,			1F		LFR, TT19S

OVERALL SHIELD, 0.536" O.D., BELDEN CAT. #9521.						MS19S

12C10TYR		TWELVE CONDUCTOR, TYREX TYPE SO, 600V, #10 AWG,				1A

STRANDED, COPPER WIRE, 1.00" O.D. NOT FOR CABLE TRAY USE.

12C12T6V		TWELVE CONDUCTOR, #12 AWG, 600V, TRAY CABLE,				1B		CA24S

UNSHIELDED, 0.685" O.D., HOUSTON WIRE & CABLE CAT.

#D0401212.

12C12TYR		TWELVE CONDUCTOR, TYREX TYPE SO, 600V, #12 AWG,				1A

STRANDED, COPPER WIRE, 0.80" O.D. NOT FOR CABLE TRAY

USE.

12C16T6V		TWELVE CONDUCTOR, #16 AWG, 600V, TRAY CABLE,				1N		LFB, MS11P

UNSHIELDED, 0.65" O.D. ALPHA CAT. #45439/12.						MS16P

12C18J		TWELVE CONDUCTORS, #18AWG, 300V, BELDEN.

12C18OS		TWELVE CONDUCTORS, #18AWG, OVERALL SHIELD.

12C18T3V		TWELVE CONDUCTORS, #18 AWG, STRANDED, TINNED COPPER.

PVC INSULATED JACKET. 0.424" O.D., BELDEN CAT#8466.

12C18TC		TWELVE CONDUCTORS, #18AWG, 300V, TRAY CABLE,

UNSHIELDED, 0.38" O.D. PVC JACKET. ALPHA CAT#1898/12.

12C18TLN		TWELVE CONDUCTORS, #18AWG, OVERALL SHIELD, 7 STR

BX .030" XLPE OAS W/22GA 7 STR TC DRAIN IN .060"

O-HALOGEN BLK JACKET LS (UL) TC 600V 90C,

LAKE CABLE # VHX1820S(LS).

12C20J		TWELVE CONDUCTOR, #20AWG, TINNED COPPER, PVC

INSULATED. 0.338" O.D. BELDEN CAT#9457.

12C22T3V		TWELVE CONDUCTOR, #22 AWG, 0.6" O.D.

MFR: MANHATTAN.

12C22T6V		TWELVE CONDUCTOR, #22 AWG, 600V, TRAY CABLE,				1N		LFR, MS26S

UNSHIELDED, 0.52 O.D.", ALPHA CAT. #45409/12.						LRR1/4

12PR16AS		TWELVE PAIRS, ARMORED CABLE, 300V, #16 AWG,				1F

STRANDED, TINNED-COPPER WIRE, OVERALL SHIELD AND DRAIN

WIRE, 1.13" O.D.,OKONITE CLX TYPE CAT-# P-OS 564-10-3412.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

12PR16OS		TWELVE PAIRS, #16 AWG, 300V, TRAY CABLE, 0.745"				1F

O.D., OVERALL SHIELDED, BELDEN CAT. #1486A.

12PR16TC		TWELVE PAIRS, #16 AWG, TRAY CABLE,

OVERALL SHIELDED.

12PR18AS		TWELVE PAIR TWISTED SHIELDED 18AWG 7 STRAND, COPPER, OKOSEAL,

PVC JACKET, 600V APPROX. OD 1.040 P/N 561-10-3312 SEQ.PRINT

12PR18IS		TWELVE PAIR, #18AWG, INDIVIDUALLY SHIELDED, TINNED

COPPER, POLYETHYLENE INSULATED, DRAIN WIRE, PVC

JACKET, 0.735"O.D., BELDEN P/N #9776.

12PR18OS		TWELVE PAIRS, #18 AWG, OVERALL SHIELDED, 300V,				1F

0.677" O.D., TRAY CABLE, BELDEN CAT. #1468A

12PR18TN		TWELVE PAIRS, INDIVIDUALLY SHIELDED, 18AWG, OVERALL SHIELD,

300V, LSZH JACKET TYPE XLPE, B/W NUMBERED PAIRS, TRAY RATED,

.649in DIAMETER, LAKE CABLE LLC, PN TXH1812PRS.

12PR20IS		TWELVE PAIRS, #20 AWG, INDIVIDUALLY SHIELDED.

12PR20OS		TWELVE PAIRS, #20 AWG, OVERALL SHIELDED, 300V,				1F

STRANDED TRAY CABLE, BELDEN CAT. #1058A.

12PR22IS		TWELVE PAIR, #22 AWG, 300V, INDIVIDUALLY SHIELDED,			1P		LFR, LRR1/4

0.464" O.D., CM RATED, BELDEN CAT. #9768.

12PR22OS		TWELVE TWISTED PAIRS, PLUS 1 SINGLE WIRE, #22 AWG,			1P		MS26PA, MS26SA

STRANDED COPPER WIRE, WITH AN OVERALL SHIELD, WITH DRAIN				MS32P, LFR

WIRE. CM RATED, SEE CONNECTOR TYPE FOR WIRING						MS19P, DAY-20

INSTRUCTIONS. 0.455" O.D., BELDEN CAT. #8312.

12PR22TN		12PR/ +1C 22GA STR TC CMG, SEMI RIGID PVC O/A AM SHIELD

65% TC BRAID SHIELD, LSZH BLK JACKET "LS" (UL) 2464,

0.487" O.D.	LAKE CABLE 03602WGP4

12PR22SS		TWELVE PAIRS, #22 AWG, 300V SOLID COPPER WIRE,				1K		MS24S, MS24P

OVERALL SHIELDED, 0.49" O.D., ALPHA CAT #3712						SOLDER

12.5PR24		TWELVE AND HALF TWISTED PAIRS, #24 AWG STRANDED TINNED

COPPER DRAIN WIRE, BELDFOIL OVERALL ALUMINUM-POLYESTER

SHIELD, TEFLON INSULATED, 0.278" O.D., BELDEN CAT.#82512.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

12PRTHRM		TWELVE PAIR, #20 AWG, PVC JACKET, COPPER-

CONSTANTAN, OVERALL SHIELD 0.592" O.D., ANSI TYPE TX.

OMEGA CAT. #12TX20PP. COLOR CODE: BLUE (COPPER+) AND RED

(CONSTANTAN-).

12SMMTLN		12-STRAND, 50/125UM, (550 METER 10-GBE), MULTI-MODE,

OPTICAL BREAKOUT CABLE.  LOW-SMOKE, ZERO-HALOGEN CABLE

SUITABLE FOR TRAYS AND RISERS. AQUA OUTER JACKET. OUTER

DIAMETER: 14MM(.55"). SUB-CABLE DIAMETER: 2.5MM(.10").

MINIMUM INSTALLATION BEND RADIUS: 21.1CM(8.3").  MINIMUM

LONG-TERM BEND RADIUS: 14.0CM(5.5").

OPTICAL CABLE CORPORATION PART NUMBER: BX012ZALE9QZ

13C22HV		THIRTEEN(BEL8869) CABLES, 22AWG, TINNED COPPER BRAID

SHIELD, BLACK PVC JACKET, PLENUM RATED, 0.645" O.D.

STORM PART#SP4433-B.

13PR28F		THIRTEEN PAIR #28AWG, FLAT/TWISTED CABLE, TINNED-

COPPER WIRE, BRAID SHIELD, PVC JACKET, 300V, 5AMP. 380" O.D.

STANDARD TWIST LENGTH IS 18" FOLLOWED BY A 2" FLAT

SECTION. BELDEN #9M28326.

15C20OS		FIFTEEN CONDUCTOR, #20 AWG, OVERALL SHIELD, 300V,			1L		DB15P

STRANDED, TRAY CABLE, 0.39" O.D., ALPHA CAT. #45470/15.

15C24OS		FIFTEEN CONDUCTOR, #24 AWG, OVERALL SHIELD, 300V,			1N		DB15P

STRANDED, TRAY CABLE, 0.33" O.D., ALPHA CAT. #45100/15.

15C24OTN		FIFTEEN CONDUCTORS, #24 AWG, OVERALL SHIELDED, TIN COPPER

BRAIDED, WITH DRAIN WIRE, LOW SMOKE ZERO HALOGEN, 300V,

O.D. = 0.315" MFG: L-COM P/N: CSLSZH15-XXX

(XXX= LENGTH OF 100, 500, 1000FT)

15PR16IS		FIFTEEN PAIR, #16AWG, INDIVIDUALLY SHIELDED, 600V,

1.125" O.D., TRAY CABLE, SUN RESISTANT, THERMO

ELECTRIC CATALOG.

15PR22IS		FIFTEEN PAIR, #22AWG, INDIVIDUALLY SHIELDED, 30V, CM			1P

RATED, 0.548" O.D., BELDEN CAT. #8776.

15PR22OS		FIFTEEN PAIR, #22 AWG, 300V, OVERALL SHIELD, TRAY			1F		LFR, TT30S

CABLE, 594" O.D., BELDEN CAT #9524.								MS32P, MS26S

MS26P, MS26PG

MS28P, MS28S

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

15PR22SS		FIFTEEN TWISTED PAIRS, #22 AWG, SOLID CONDUCTORS,

INDIVIDUALLY SHIELDED, CM RATED, 300V, 0.525" O.D.,

BELDEN CAT #8766.

15PR22TS		FIFTEEN PAIRS, #22 AWG, 300V, 7 TC STRANDS,

OVERALL SHIELD, TRAY CABLE. 0.594" O.D. BELDEN CAT#9524.

16C22OS		SIXTEEN CONDUCTORS, #22 AWG, OVERALL SHIELDED.

16PR16AS		SIXTEEN PAIR, #16 AWG, 300V, ARMORED SHIELD, 1.26"			1F

O.D., TRAY CABLE, OKONITE CAT. #564-10-3416.

16PR16IS		SIXTEEN PAIR, #16 AWG, 600V, TRAY CABLE, INDIVIDUALLY			1F		LFB

SHIELDED 1.023" O.D., BELDEN CAT. #1043A.

16PR16OS		SIXTEEN PAIR, #16 AWG, 600V, OVERALL SHIELDED, TRAY			1F

CABLE, BELDEN CAT. #1073A.

16PR20AS		SIXTEEN PAIRS, #20 AWG, ARMORED CABLE, 300V,				1F

STRANDED, TRAY CABLE, 1.03" O.D., OKONITE CAT. #564-10-3216.

16PR20KT		16-PAIR, K-TYPE THERMOCOUPLE EXTENSION CABLE.

20AWG, SOLID CONDUCTORS.POSITIVE WIRE: YELLOW.

NEGATIVE WIRE: RED.  ALUMINUM/MYLAR OVERALL

SHIELD WITH DRAIN WIRE.  OMEGA PART NUMBER 16KX20PP.

17PR28RF		SEVENTEEN PAIR, #28AWG, PVC SHIELDED, ROUND-TO-FLAT,

300V RMS,0.050" PITCH MASS-TER CABLE. BELDEN CAT.#9M-28334.

18MTW			ONE CONDUCTOR, #18AWG, STRANDED, WIRE TYPE MTW,

TFF, AWM, TEW, 600V, 6AMPS, 500 FEET SPOOL, GRAINGER.

18PR22OS		EIGHTEEN TWISTED PAIRS, 300V, #22 AWG, STRANDED,			1J		AMP36P,LFR,D37S,

COPPER WIRE, OVERALL SHIELD WITH DRAIN WIRE, 0.54" O.D.,				D37P,LFB,DB52S,

SLAC SPECIAL SLAC S/N61-329-326-19.MFG. GORE, OR EQUAL.				AMP48P,MS19S,TT30P,

DD50S,UVC90

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

18PR22TN		EIGHTEEN TWISTED PAIRS, # 22 AWG, STRANDED, COPPER WIRE

OVERALL SHIELD WITH DRAIN WIRE, LSZH JACKET, 0.50" O.D.

SPECIAL ORDER, MFG: BELDEN, P/N: Y52530.

NOTE: Any termination of this cable with an AMP36P

Connector is to be done as indicated on drawing CA-123-693-00.

The drawing exceptions are:

1) Use the length as appropriate for the indicated

cable, and

2) Label the cable with the SLAC-Standard computer

Generated labels.

18PR24IS		EIGHTEEN PAIRS, #24 AWG, INDIVIDUALLY SHIELDED.

18PR28OS		EIGHTEEN TWISTED PAIRS, #28 AWG, STRANDED, CL2 RATED,			1P

OVERALL SHIELD WITH DRAIN WIRE. 0.365" O.D.,BELDEN CAT #9819

19C12T6V		NINETEEN CONDUCTOR, #12 AWG, 600V, TRAY CABLE,				1B		LRY

UNSHIELDED, 0.800" O.D., HOUSTON WIRE&CABLE CAT.#D0401219.

19C16/3V		NINETEEN CONDUCTOR, #16 AWG.

19C16T3V		NINETEEN CONDUCTOR, #16AWG, 300V, STRANDED.

19C16T6V		NINETEEN CONDUCTOR, #16 AWG, 600V, TRAY CABLE,				1N		MS16P,LFB

UNSHIELDED, 0.74" O.D., ALPHA CAT. #45439/19.

19C18OS		NINETEEN CONDUCTOR, #18 AWG, 600V, TRAY CABLE,				1N		LFR, MS20P

OVERALL SHIELD, 0.64" O.D., ALPHA CAT. #45430/19.

19C18T6V		NINETEEN CONDUCTOR, #18 AWG, 600V, TRAY CABLE,				1N		TT19SM TT19P

UNSHIELDED, 0.68" O.D., ALPHA CAT. #45429/19						LFR

19C22TEF		NINETEEN CONDUCTORS, #22AWG, TINNED COPPER CONDUCTORS, FEP

TEFLON INSULATION, TEFLON JACKET, RED TINT, 0.269" O.D.

BELDEN CAT#83569.

19PR18OS		NINETEEN PAIR, #18 AWG, 300V, OVERALL SHIELD, 0.75"			1H

O.D. ALPHA CAT. #45379/19.

19PR22IS		NINETEEN PAIR, #22 AWG, 300V, INDIVIDUALLY SHIELDED,			1F		MS41P, MS41S

TRAY CABLE, 0.686" O.D., BELDEN CAT. #9335.						LFR, VIK-44,PUSHON

19PR22OS		NINETEEN PAIR, #22 AWG.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

19PR24OS		NINETEEN PAIR, #24 AWG, 300V, OVERALL SHIELDED, CM RATED,		1P		MS32P, MS32S

0.448" O.D., BELDEN CAT#9519.

20C20OS		TWENTY CONDUCTORS, #20 AWG, 300V, OVERALL					1L		LFR, MS32S

SHIELDED, TRAY CABLE,0.43" O.D., ALPHA CAT. #45470/20.				MS10P

24PR16AS		TWENTY-FOUR PAIR, #16 AWG, 300V, ARMORED SHIELD, TRAY			1F

CABLE, 1.53" O.D., OKONITE CAT#564-10-3424.

24PR16OS		TWENTY-FOUR PAIR, #16 AWG, OVERALL SHIELD, 600V, TRAY			1F

CABLE, 1.147" O.D., BELDEN CAT. #1074A.

24PR16TC		TWENTY-FOUR PAIR, #16 AWG, TRAY CABLE.MFR: OKONITE.

24PR18AS		24 PAIR TWISTED SHIELDED 18AWG 7 STRAND, COPPER, OKOSEAL,

PVC JACKET, 600V APPROX. OD 1.350 P/N 561-10-3324 SEQ.PRINT

24PR18IS		TWENTY-FOUR PAIR, #18 AWG, 300V, INDIVIDUALLY SHIELDED,		1F

TRAY CABLE,1.025" O.D., BELDEN CAT. #1480A.

24PR18OS		TWENTY-FOUR PAIRS, #18 AWG, OVERALL SHIELDED, TRAY CABLE,		1F

600V, BELDEN CAT.#1068A. 1.027" O.D.(300V FROM ANIXTER)

24PR18TC		TWENTY-FOUR PAIRS, #18 AWG, TRAY CABLE, OVERALL SHIELDED.

24PR20TC		TWENTY-FOUR PAIRS, #20 AWG, TRAY CABLE.

24PR22IS		TWENTY FOUR PAIR, #22 AWG, INDIVIDUALLY SHIELDED, CM			1F

RATED, 0.891" O.D., BELDEN CAT. #1821A.

24PR20SS		TWENTY-FOUR PAIR, #20 AWG, OVERALL SHIELDED, SOLID WIRE,

0.875" O.D.

24PRTHRM		TWENTY-FOUR PAIR, #20 AWG, PVC JACKET, COPPER

CONSTANTAN, OVERALL SHIELD, 0.770" O.D., ANSI TYPE TX.

OMEGA CAT. #24TC20PP. COLOR CODE: BLUE (COPPER +)

AND RED(CONSTANTAN -).

25C16T3V		TWENTY-FIVE CONDUCTORS, #16 AWG, 300V, STRANDED, TRAY			1L

CABLE 0.66" O.D., ALPHA CAT. #45080/25.

25C16T6V		TWENTY-FIVE CONDUCTORS, #16 AWG, 600V, UNSHIELDED

TRAY CABLE. 0.93" O.D. ALPHA CAT#1085.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

25C20OS		TWENTY-FIVE CONDUCTORS, #20 AWG, OVERALL SHIELD,			1L		DB15P

300V, TRAY CABLE, O.47" O.D., ALPHA CAT.#45470/25.

25C20TN           TWENTY-FIVE CONDUCTORS, #20 AWG, SHIELDED, LOW SMOKE ZERO HALOGEN,

300V, TRAY CABLE, O.D. 0.502 IN.

MFG: LAKE CABLE, P/N: TXH2026S.

25C24OS		TWENTY-FIVE CONDUCTORS, #24 AWG.

25C26OS		TWENTY-FIVE CONDUCTORS, #26 AWG.

25C28F		TWENTY-FIVE CONDUCTOR, #28 AWG, FLAT RIBBON CABLE,

STRANDED TINNED COPPER WIRE, WITH GRAY PVC INSULATION,

RED POLARITY STRIPE. 0.050 PITCH NOMINAL WIDTH 1.25",

300V RATING, BELDEN CAT. #9L28025. NOT CABLE TRAY RATED.

25PR19SS		TWENTY-FIVE PAIR, #19 AWG, SOLID CONDUCTORS, OVERALL					LFR

SHIELD, 1.0" O.D.

25PR22OS		TWENTY-FIVE PAIR, #22 AWG, OVERALL SHIELDED, 300V			1P

STRANDED TINNED COPPER, 0.620: O.D., CM RATED, BELDEN CAT.

#8325.

25PR24IS		TWENTY-FIVE PAIRS, DATA TRANSMISSION CABLE, #24 AWG,			1P

INDIVIDUALLY SHIELDED, CM RATED, 0.94" O.D., BELDEN

CAT. #8185.

25PR24OS		TWENTY-FIVE PAIRS, #24 AWG, 300V, STRANDED, CM RATED,			1P

OVERALL SHIELDED, 0.708" O.D., BELDEN CAT. #9550.

25PR24SR		TWENTY-FIVE PAIRS, #24 AWG, TINNED COPPER, S-R PVC

INSULATED, TWISTED PAIRS, OVERALL BELDFOIL ALUM-POLY SHIELD,

CHROME PVC JACKET, 300V, 0.503" O.D., BELDEN CAT.#9525.

25PR24SS		TWENTY-FIVE PAIRS, #24 AWG, OVERALL SHIELDED, SOLID					PUSHON

CONDUCTORS, REA PE-22, TELEPHONE CABLE O.55" O.D.,

ANIXTER E-002524AAC

25PR28OS		TWENTY-FIVE TWISTED PAIRS, #28 AWG, STRANDED, CL2 RATED,

OVERALL SHIELD WITH DRAIN WIRE.0.429" O.D.,BELDEN CAT#9825

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

25PRCAT5		TWENTY-FIVE PAIRS, #24 AWG, TIA/EIA 568-A CAT 5,

OVERALL SHIELDED, SCREENED TWISTED PAIR (ScTP).

THERMOPLASTIC, GRAY PVC .522" O.D.

NON-PLENUM, MOHAWK PART NO.# M56832

25PCAT5E		TWENTY-FIVE PAIRS, #24 AWG, TIA/EIA 568-A CAT 5E,

OVERALL SHIELDED. THERMOPLASTIC, GRAY PVC .470" O.D.

NON-PLENUM, MOHAWK PART NO.# M58141

26C16/3V		SAME AS 3C16/3V EXCEPT: TWENTY-SIX CONDUCTORS, 0.7"O.D.		1A		LFB, MS11S, MS21P,

MS26P, MS26S, TT19P,

MS21S, LFR

26C22/3V		SAME AS 3C16/3V EXCEPT: TWENTY-SIX CONDUCTORS, #22 AWG,		1A		LFR, MS19S

0.7" O.D.

26C22OS		TWENTY-SIX CONDUCTORS, #22 AWG, OVERALL SHIELDED.

26C24OS		TWENTY-SIX CONDUCTOR, #24 AWG, STRANDED TINNED				1N		DB25S, DB25P

COPPER WIRE, 0.38" O.D. SLAC S/N61-329-326-26.

26PR22OS		TWENTY-SIX TWISTED PAIRS, 300V, #22 AWG, STRANDED, COPPER		1A

WIRE, OVERALL SHIELD WITH DRAIN WIRE, LBL SPEC. LBL-95-10E.

0.5" O.D.

27C20OS		TWENTY-SEVEN CONDUCTORS, #20 AWG, STRANDED				1N

COPPER, OVERALL SHIELD,CM RATED, 300V, 0.52" O.D.,ALPHA

NO.5565C.

27C22TC		TWENTY-SEVEN CONDUCTOR, #22 AWG, STRANDED, 300V,			1N

UNSHIELDED, CM RATED, 0.45" O.D., ALPHA CAT. #5215C.

27PR22OS		TWENTY-SEVEN PAIR, #22 AWG, 300V, OVERALL SHIELD, 0.741"		1F		LFR, SOLDER

O.D., TRAY CABLE, BELDEN CAT. #9527.

27PR24IS		TWENTY-SEVEN PAIRS, #24 AWG, 300V, INDIVIDUALLY SHIELDED		1P

CM RATED, 0.797" O.D., BELDEN CAT. #9738.

28P22OSS		SLAC MADE, 28 TWISTED PAIRS OF 22 AWG,TINNED STRANDED COPPER.

WIRES ARE TFE INSULATED (RED/WHITE). WIRES ARE THEN WRAPPED

IN STRANDED,TINNED COPPER EXPANDABLE WIRE TUBES

(.38 DIAMETER TYP.- MIL-SPEC INC P/N 2146)AND THEN WRAPPED

IN STRANDED EXPANDABLE POLYETHYLENE TUBES

(ALTA TECH, 1" DIA PE FLEXIBLE TUBE).

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

30PR26OS		THIRTY PAIR, #26 AWG, STRANDED OVERALL SHIELDED, 0.5"					AMP48P

O.D. SLAC S/N61-329-326-30, GORE CAT.#RCN2294-REV-A.

32C18OS		32 CONDUCTORS 18AWG OVERALL SHIELD LOW SMOKE ZERO HALOGEN

CABLE TRAY RATED, RAYCHEM # EPD-RWC-20078-L022.

32C18TLN		THIRTY-TWO CONDUCTOR, #18AWG STRANDED TINNED COPPER,

300V TRAY CABLE,ZERO HALOGEN.0.611”O.D.,WT=0.288LBS/

FT.RAYCHEM WCD51/1611.

34PRSCSI		68 PIN CONN OVER SHIELDED PLUG WITH ASSEMBLED STANDARD				SCSI68P

TERMINATION COVERS. AMPLIMITE SERIES III THERMOPLASTIC.

AMP PART # 68KEK00051.

36PR16AS		C-L-X® TYPE SP-OS TYPE ITC/PLTC ARMORED INSTRUMENTATION

CABLE MULTIPLE SHIELDED PAIRS OR TRIADS-METAL JACKET

OVERALL SHIELD 600 VOLTS - 105°C RATING FOR CABLE TRAY USE

OKONITE P/N 561-60-3436 O.D. 1.53".

36PR16OS		THIRTY-SIX PAIR, #16 AWG, 300V, OVERALL SHIELDED, TRAY		1F

CABLE, 1.184" O.D., BELDEN CAT. #1494A.

36PR18TN		THIRTY-SIX PAIR TWISTED SHIELDED, 7 STR BC LSXLPE

O/A SHIELD 300V PLTC  LAKE CABLE P/N TXH1836RPS O.D. 1.023in.

UL listed as Type PLTC per UL standard 13 IEEE 383, UL 2250,

& 1581(1685)

36PR18OS		THIRTY-SIX PAIR, #18 AWG, 300V, STRANDED, OVERALL SHIELD,		1F		LFR

TRAY CABLE, 1.062" O.D., BELDEN CAT. #1472A.

37C24OS		THIRTY-SEVEN CONDUCTORS, #24 AWG LLL CABLE.

37C24TEF		EIGHTEEN AND ONE-HALF PAIRS, #24AWG TINNED COPPER,

FOAM INSULATED, TWISTED PAIRS. OVERALL BELDFOIL

ALUMINUM-POLYESTER SHIELD 24 AWG STRANDED TINNED

COPPER DRAIN WIRE. GRAY FLUOROCOPOPOLYMER JACKET,

300V, NEC ARTICLE 800, 0.484"O.D. BELDEN P/N 88118.

37C28FLT		THIRTY-SEVEN CONDUCTOR, #28AWG, FLAT RIBBON CABLE			1a

STRANDED TINNED COPPER, NORMAL WIDTH 1.85", 300V,

0.50" PITCH, BELDEN CAT.#9R28037.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

40C18T3V		FORTY CONDUCTORS, #18 AWG, 300V, STRANDED, TINNED COPPER		1L		LFR

WIRE, UNSHIELDED, TRAY CABLE, 0.69" O.D., ALPHA CAT.

#45070/40.

40C24OS		FORTY CONDUCTOR, #24 AWG, 300V, OVERALL SHIELD, CM			1A		3M40S

RATED 0.430" O.D., BELDEN CAT. #9545.

40C28FOS		FORTY CONDUCTOR, #28 AWG, FLAT RIBBON CABLE, SHIELDED					D37P

AND JACKETED,TWISTED PAIR, PVC/PVC, TINNED STRANDED

COPPER, 3M P/N 1785/40.

40PR18AS		50PR16AS DESCRIPTION: C-L-X® TYPE SP-OS TYPE ITC/

PLTC ARMORED INSTRUMENTATION CABLE MULTIPLE SHIELDED PAIRS

OR TRIADS-PVC JACKET OVERALL SHIELD 300 VOLTS-105ºC RATING

FOR CABLE TRAY USE OKONITE P/N 561-10-3450.

50C28FOS		FIFTY CONDUCTOR, #28 AWG, FLAT RIBBON CABLE, SHIELDED

AND JACKETED,TWISTED PAIR, PVC/PVC, TINNED STRANDED

COPPER.

50C16T3V		FIFTY CONDUCTOR, #16 AWG, 300V, 0.93" O.D., UNSHIELDED,		1L		LFB

TRAY CABLE, ALPHA CAT. #45080/50.

50C16OS		FIFTY CONDUCTOR, #16 AWG, 300V, OVERALL SHIELD,				1L		LFB

TRAY CABLE 0.93" O.D. ALPHA CAT. #45370/50.

50C18OS		FIFTY CONDUCTOR, #18 AWG, 300V, TRAY CABLE,				1L		LFB, BULLET

OVERALL SHIELD, 0.76" O.D., ALPHA CAT. #45390/50.

50C18TLN		50C/18GA 7STR BC XLPE, OAS W/ 20GA 7STR TC DRAIN IN

0-HAL BLK JACKET "LS" (UL) TC 600V 90C, 80MILS,

1.573”O.D. AMERCABLE GEXOL-HF.

50C20OS		FIFTY CONDUCTOR, #20 AWG, OVERALL SHIELD, 300V,				1L		LFR

0.67" O.D., ALPHA CAT. #45470/50.

50C24IS		FIFTY CONDUCTOR, #24 AWG, INDIVIDUALLY SHIELDED TELCO.

50PR16AS		SAME AS 4PR16AS EXCEPT: FIFTY PAIRS, 1.98" O.D.,			1F

OKONITE CLX TYPE P-OS 564-10-3450

50PR16OS		FIFTY PAIRS, #16 AWG, 600V, OVERALL SHIELDED, TRAY CABLE,		1F

1.598" O.D., BELDEN CAT. #1090A.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

50PR16TC		FIFTY PAIRS, #16 AWG, TRAY CABLE. MFR: OKONITE.

50PR18AS		FIFTY PAIRS, #18 AWG, ARMORED CABLE, 300V, OVERALL			1F

SHIELDED,WITH DRAIN WIRE, 1.72" O.D., OKONITE CLX TYPE

P-OS P/N 564-10-3350.

50PR18OS		FIFTY PAIR, #18 AWG, 600V, OVERALL SHIELDED, TRAY CABLE,		1F

1.456" O.D., BELDEN CAT.#1088A.

50PR22S		FIFTY PAIRS, #22 AWG, SOLID COPPER WIRE, UNSHIELDED,

0.50"O.D. PLENUM CABLE.

50PR24NS		FIFTY PAIRS,#24 AWG, NO SHIELD. PVC JACKET.

TELEPHONE WIRE.

50PR24OS		FIFTY PAIR, #24 AWG, OVERALL SHIELDED.

50PR24SS		FIFTY PAIRS, #24 AWG, SOLID COPPER WIRE, OVERALL SHIELD,

SOLID CONDUCTORS, REA PE22, 0.70" O.D., ANIXTER E-005024AAA.

51PR22OS		FIFTY-ONE TWISTED PAIRS, #22 AWG, ANNEALED COPPER WIRE		1X

OVERALL SHIELD WITH DRAIN WIRE, 300V, 1.00" O.D.,

MFG. SLAC SPECIFICATION #PS 114-001-01-R3.

51PR22SS		FIFTY-ONE TWISTED PAIRS, #22 AWG, SOLID CONDUCTOR,			1P

OVERALL SHIELD WITH DRAIN WIRE, 300V, 0.710" O.D., CM

RATED, BELDEN CAT #8751.

52C16/3V		FIFTY-TWO CONDUCTOR, #16 AWG, 300V, UNSHIELDED, 1.00"			1A		LFB

O.D., MFR UNKNOWN.

55C22OS		FIFTY-FIVE CONDUCTOR, #22 AWG, 600V, OVERALL						LFR, SOLDER

SHIELDED 0.75" O.D. MFR UNKNOWN.

60C16OS		SIXTY CONDUCTOR, #16 AWG, OVERALL SHIELDED, 300V,			1L

TRAY CABLE, 1.00" O.D., ALPHA CAT. #45370/60.

100PR24S		ONE HUNDRED PAIRS, #24 AWG, OVERALL SHIELDED, SOLID					PUSHON

CONDUCTORS, REA PE-22, TELEPHONE CABLE, 0.87" O.D.,

ANIXTER E-010024AAC.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

262FLX		DIESEL LOCOMOTIVE CABLE,

MINIMUM WIRES PER CONDUCTOR 646, NOMINAL OUTSIDE DIAMETER IN 0.973,

APPROX. WEIGHT LBS. PER 1,000 FT. 1436, AMPACITY 90DEG. 591,

EXTRA FLEXIBLE CABLE, 600V,

STORES ID: 146102

PART # AMERCABLE 37-119-215,

PLEASE SEE GENERAL NOTES # 8

AC-BM1		AC LINE CORD FOR EXISTING BUSINESS MACHINES.						PH290B, SPH386

PREWIRED WITH MOLDED CONNECTORS. BELDEN P/N 17952, #16

AWG,3 CONDUCTOR, 13A, SLAC P/N61-329-704-01.

AC-BM2		AC LINE CORD FOR EXISTING BUSINESS MACHINES

PREWIRED WITH MOLDED CONNECTORS. ONE END HAS A PH290B

CONNECTOR AND THE OTHER END HAS A SPH386. BELDEN P/N

17255C, #16 AWG, 3 CONDUCTOR,13A, SLAC P/N61-329-704-02.

BWRB12		A SET OF 4 WIRES CONSISTING OF ONE EACH OF THE

FOLLOWING: #12-BLK, #12-RED, #12-BLU AND #12-WHT. THIS IS

TREATED AS A SINGLE CABLE.

C195X08T		A SET OF 8 CNT195FR CABLES USED IN ONE BUNDLE,

TYPICALLY FOR USE IN A TRUNK OR BACKBONE APPLICATION

FROM PATCH PANEL TO PATCH PANEL.

CAMLNK10		CUSTOM COMMERCIAL CABLE, P/N # CLCP-10-P#3179,INTERCON 1

NORTECH SYSTEMS.

CAT6TLN		CATEGORY 6 LSZH UTP SOLID & STRANDED CABLES HORIZONTAL CABLE:

1*24AWG SOLID COPPER POLYOLEFIN INSULATION & FILLER,

JACKET: LSZH,UL-E151955/CSA-LL79189/ETL Cable Master.236" OD

CAT6STLN	   CATEGORY 6, 26 AWG TINNED COPPER (STRANDED), OVERALL SHIELD,

LOW SMOKE, ZERO HALOGEN JACKET,JACKET COLOR LIGHT GRAY,

0.24" O.D. (NOMINAL).

CAT6X06R	  	6X CAT6 CABLES SPIRAL WRAPPED AS ONE BUNDLE MANF HELLERMAN TYTON,

RAPIDNET, 23 AWG STRANDED RISER CABLE, BLUE PART # RNGC06ARBCZXXX, XXX

IS THE CABLE FOOTAGE, Z IS TERMINATION FOR THE SECOND END (REFER TO HELLERMAN TYTON FOR OPTIONS)

EACH CAT6 IS DIAMETER 6.2MM, OVERALL BUNDLE IS ABOUT 18.5MM.

CAT6X06T	   6 X CAT6 BACKBONE TRUNK CABLES. EACH CABLE IN THE BUNDLE IS

MADE OF CAT6STLN CABLES.

CAT6X12T	   12 X CAT6 BACKBONE TRUNK CABLES. EACH CABLE IN THE BUNDLE IS

MADE OF CAT6STLN CABLES.

CAT6X24T	   24 X CAT6 BACKBONE TRUNK CABLES. EACH CABLE IN THE BUNDLE IS

MADE OF CAT6STLN CABLES.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

CAT6X48T	   48 X CAT6 BACKBONE TRUNK CABLES. EACH CABLE IN THE BUNDLE IS

MADE OF CAT6STLN CABLES.

CONVGAU1		SPECIAL PREWIRED CABLE ASSEMBLY FOR A CONVECTRON VAC

GAUGE. THERE IS AN AMP15P CONNECTOR ON ONE END AND A

GP5S ON THE OTHER END. THIS CABLE IS SUPPLIED BY THE

CONTROLS VACUUM GROUP.

CNT100FR		.110" COAX, 50 OHM IMPEDANCE, FOAM DIELECTRIC,LSZH JACKET,

MAX FREQ 61.00 GHZ, ANDREW CINTH CABLE P/N CNT100FR .

CNT195		COAXIAL CABLE, 50 OHMS, CAPACITANCE 24 PF/FT, 0.195” O.D.,

NON-HALOGEN, FLAME RETARDANT POLYOLEFIN,

(NOT: LOW SMOKE OR TRAY RATED),MFG: ANDREW, P/N: CNT-195-FR.

CNT195FR		.195" COAX, 50 OHM IMPEDANCE, FOAM DIELECTRIC,LSZH JACKET,

MAX FREQ 37.9 GHZ, (SEE LMR195FR FOR EQUIVALENT)

ANDREW CINTH CABLE P/N CNT195FR.

DB9MFV		PRE-FABRICATED COMPUTER CABLE D-SUB 9 PIN MALE TO FEMALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPPLIERS, IE. "FRY'S ELECTRONICS"

DB9MMV		PRE-FABRICATED COMPUTER CABLE D-SUB 9 PIN MALE TO MALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS, IE. "FRY'S ELECTRONICS"

DB25MFV		PRE-FABRICATED COMPUTER CABLE D-SUB 25 PIN MALE TO FEMALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPPLERS, IE. "FRY'S ELECTRONICS"

DB25MMV		PRE-FABRICATED COMPUTER CABLE D-SUB 25 PIN MALE TO MALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPPLERS, IE. "FRY'S ELECTRONICS

DC-BUS		THIS INDICATES A SPECIAL LARGE CONDUCTOR, OFTEN

WATER-COOLED, NORMALLY USED FOR THE CONNECTION OF

HIGH-CURRENT MAGNETS. THE ACTUAL CONDUCTOR WILL BE

SPECIFIED ON THE INSTALLATION DRAWING, OR IN THE

INSTALLATION INSTRUCTIONS, FOR THAT PARTICULAR SYSTEM.

DS2124		SINGLE CONDUCTOR, SHIELDED, #16 AWG, 100VDC, 0.440"

O.D., DIELECTRIC SCIENCES P/N 2124.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

ELOCAB		TWO CONDUCTORS, #22AWG, (RED&BLACK),AND 2 TWO CONDUCTOR

#XXAWG STRANDED WITH BRAIDED SHIELD. ROUND CABLE, 150V,

OVERALL FOIL SHIELD WITH BRAID SHIELD, BENDING RADIUS 2

TIMES DIAMETER, X.XXX" O.D., ELOCAB P/N ERK 4181.

EXT-10		AC EXTENSION CORD, U-GROUND, 10' LONG, #16 AWG, 3

CONDUCTOR, MALE PLUG ON ONE END, FEMALE PLUG ON THE

OTHER END, SJO OR SJ CORD, MOLDED PLUGS, SLAC

P/N 61-329-702-05.

FBMH4002		TWO FIBER OPTIC, MEGA POLYETHYLENE JACKET OPTICAL FIBER CORD

CORE MATERIAL: POLYMETHYL METHACRYLATE RESIN (PMMA),

CLADDING MATERIAL: FLUORINATED POLYMER,

JACKET DIMENSION-MINOR AXIS UNIT MM, TYPICAL 2.2

JACKET DIMENSION-MAJOR AXIS UNIT MM, TYPICAL 4.4

APPROXIMATE WEIGHT UNIT G/M, TYPICAL 7.5

MINIMUM BEND RADIUS: LOSS INCREMENT =<0.5DB {A QUARTER BEND} UNIT MM, VALUES MIN.25

TENSILE STRENGTH: TENSILE FORCE AT 5% ELONGATION; IN CONFORMITY TO THE JIS C 6861,

UNIT N, VALUES MIN.140 COLOR AND MATERIAL: BLACK, POLYETHYLENE.

INDICATION ON JACKET: ESKA MEGA; PINK.

MANUFACTURE BY MITSUBISHI RAYON. PART # MH4002

FIBOPT		FIBER OPTIC CABLE, MFR: ANIXTER.

FIBOPT1		FIBER OPTIC CABLE ASSEMBLY,THIS CABLE IS FACTORY					OPTIC

TERMINATED WITH SMA-TYPE CONNECTORS. CABLE IS ORDERED

IN SPECIFIC LENGTHS, KINETIC SYSTEMS CAT #5802-D201,

O.242" O.D. THIS CABLE IS TO BE TERMINATED BY QUALIFIED

PERSONNEL ONLY.

FIBOPT2		MULTI-FIBER, 2 FIBERS, CORE/CLADDING DIAMETER IS

100/140, CABLE TYPE 2, CABLE O.D.= .11X.21. THIS IS A

CABLE ASSEMBLY ORDERED IN SPECIFIC LENGTHS WITH ST-TYPE

CONNECTORS, ANNIXTER CAT. #370-047-100-/140SP-2.

FIBOPT3		MILTI-FIBER, 2 FIBERS, CABLE TYPE 2, DFNP PLENIUM					SC&ST

RATED, MAX. Att. 3.75/1.5dB/km. MINIMUM BEND RADIUS 2.0

INCHES. MFR SIECOR P/N 002K58-31141-24. ANIXTER P/N

370-148-62SJ-2.

FIBOPT4		ONE CONDUCTOR, ZERO HALOGEN, 0.102" O.D.,

MFG EUROFO, P/N FT2G0037.

FIBOPT5		EIGHT FIBER, PLENUM (OFNP), MULTIMODE, MAXIMUM

ATTENUATION. 850 n m/3.75 to 1300 n m/1.2 DB/KM.

0.410" O.D. MFG 3M THRIFTY-BIT.

FIBOPT6		SINGLE FIBER, PLENUM RATE, MFR: 3M #FT-400-EMT.

FIBOPT06		SINGLE MODE 6 STRAND, RADIATION RESISTANT, LOOSE TUBE,

LSZH (FRPE), FUJIKURA P/N LL006ALC5101N1, SPEC. DNL-3224

CABLE DIAMETER .469 IN.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

FIBOPT7		MULTI-FIBER,24 FIBERS IN 4 SUB UNITS, 900UM, TIGHT BUFFER				ST,SC

W/EPOXY GLASS ROD & ARAMID FIBER YARN, FLAME-RETARDANT

PVC, ORANGE JACKET, 20 X O.D. MIN. BEND RADIUS

(INSTALLATION),(UL) LISTED TYPE OFNR,.529". O.D., GENERAL

CATALOG # XX0241 AIR.

FIBOPT8		50/125 µM, 24MM, 12 SM HYBRID VERSION, PE INNER AND

OUTER JACKETS, 3.0 MM BUFFER TUBE, ULTRAVIOLET-RESISTANT,

FLAME RETARDANT, ZERO HALOGEN,IEEE-383 COMPLIANT,LISTED

OFN-LS AND CSA FT4-ST1, CABLE TRAY RATED.

CORNING CABLE SYSTEMS.

FIBOPT9		50/125 µM, DUPLEX MM, PE INNER AND OUTER JACKETS, 3.0 MM

BUFFER TUBE, ULTRAVIOLET RESISTANT, FLAME RETARDANT, ZERO

HALOGEN, IEEE-383 COMPLIANT, LISTED OFN-LS AND CSA FT4-ST1,

CABLE TRAY RATED. CORNING CABLE SYSTEMS.

FIBOPT10		50/125 µM, 48MM, 24 SM HYBRID VERSION, PE INNER AND

OUTER JACKETS, 3.0 MM BUFFER TUBE, ULTRAVIOLET-RESISTANT,

FLAME RETARDANT, ZERO HALOGEN,IEEE-383 COMPLIANT, LISTED

OFN-LS AND CSA FT4-ST1, CABLE TRAY RETED.

CORNING CABLE SYSTEMS.

FIBOPT11		COMMERCIAL CABLE, VENDOR TYCO ELECTRONICS, LIGHTRAY MPO,

OPTIMATE, 12 – 50/125 MICRON FIBERS, OFNP, DRG. NO. C-1435028.

DIAMETER OF THE CABLE AT 0.25”

FIBOPT12	   (FORMALLY 6 STRAND RAD HARD FUJIKURA),SINGLE MODE,12 STRAND,

RADIATION RESISTANT, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL006ALC510N1, SPEC. DNL-3224 CABLE DIAMETER .469 IN.

FIBOPT13	   SINGLE MODE, 48 STRAND, RADIATION RESISTANT, LOOSE TUBE,

LSZH (FRPE),FUJIKURA P/N LL0048ALC510N1, SPEC. DNL-3225

CABLE DIAMETER .??? IN.

FIBOPT14	   SINGLE MODE, 72 STRAND, RADIATION RESISTANT, LOOSE TUBE,

LSZH (FRPE),FUJIKURA P/N LL0072ALC610N1 SPEC. DNL-3226

CABLE DIAMETER .??? IN.

FIBOPT24		SINGLE MODE 24 STRAND, RADIATION RESISTANT, LOOSE TUBE,

LSZH (FRPE), FUJIKURA P/N LL024ALC5101N1, SPEC. DNL-3224

CABLE DIAMETER .469 IN.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

FIBOPT48		(FORMALLY 13 STRAND RAD HARD FUJIKURA) SINGLE MODE

48 STRAND,RADIATION RESISTANT, LOOSE TUBE, LSZH (FRPE),

FUJIKURA P/N LL048ALC5101N1, SPEC. DNL-3225 CABLE

DIAMETER .469 IN.

FIBOPT72		(FORMALLY 14 STRAND RAD HARD FUJIKURA) SINGLE MODE

72 STRAND,RADIATION RESISTANT,LOOSE TUBE, LSZH (FRPE),

FUJIKURA P/N LL072ALC6101N1, SPEC. DNL-3226 CABLE

DIAMETER .500 IN.

FIBOPT96		SINGLE MODE 96 STRAND, RADIATION RESISTANT, LOOSE TUBE,

LSZH (FRPE), FUJIKURA P/N LL096ALC8101N1, SPEC. DNL-3226

CABLE DIAMETER .571 IN.

FIBOSM02		SINGLE MODE 02 STRAND, LOOSE TUBE, LSZH (FRPE), AFL

Telecommunications P/N KE0029481801 SM, .469 IN Max.

tensile load short term 600lbs, long term 200lbs,

77lbs per 1000ft nominal weight. Minimum bend radius

Short term 9.4in., Long term 4.7in SINGLE JACKET OFNG-LS LISTED

FIBOSM06		SINGLE MODE 06 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA P/N

LL0069C5101N1, SPEC. DNL-3224 CABLE DIAMETER .469 IN.

(FORMALLY CALLED A FIBOPT12 ON LTIM01 WHICH WAS ALSO CALLED

A RAD HARD 6 STRAND)

FIBOSM12		SINGLE MODE 12 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL0129C5101N1, SPEC. DNL-3224 CABLE DIAMETER .469 IN.

FIBOSM24		SINGLE MODE 24 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL0249C5101N1, SPEC. DNL-3224 CABLE DIAMETER .469 IN.

FIBOSM48		SINGLE MODE 48 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL0489C5101N1, SPEC.DNL-3224 CABLE DIAMETER .469 IN.

FIBOSM72		SINGLE MODE 72 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL0729C6101N1, SPEC.DNL-3224 CABLE DIAMETER .500 IN.

FIBOSM96		SINGLE MODE 96 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL0969C8101N1, SPEC.DNL-3224 CABLE DIAMETER .571 IN.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

FIBOSMPG		FIBER OPTIC, SINGLE MODE, TIGHT BUFFERED STRAND WITH A

FACTORY INSTALLED CONNECTOR ON ONE END AND CUT FIBER ON

THE OTHER FOR FUSION OR MECHANICAL SPLICING. USUALLY PART

OF A MODULE. PIGTAIL TYPICAL LENGTHS ARE 1 OR 2 METERS.

WHEN CODED IN CAPTAR, PIGTAIL LENGTHS ARE ADDED TO FIBER

SHEATH LENGTHS FOR A TOTAL PATH LENGTH.

TYPICAL P/N: SYSTIMAX MODG2-12LC-SM-PT.

FIBSM144		SINGLE MODE 144 STRAND, LOOSE TUBE, LSZH (FRPE), FUJIKURA

P/N LL1449CC101N1, SPEC. DNL-3224 CABLE DIAMETER .720 IN.

FIB1310		SINGLE MODE, BARE FIBER STRAND. ALWAYS PART OF A LARGER FIBER

CABLE OR SHEATH. 1310 INDICATES 1310 NANOMETER OF OPERATION

BASED ON STANDARD CORNING FIBER SPECIFICATIONS AND COLOR

CODED TO STANDARD FIBER METHODS. STRAND DEFINITIONS REQUIRED

FOR SPLICING INFORMATION PURPOSE AND NO PART NUMBERS ARE

FIOPHYB		HYBRID FIBER OPTIC CABLE, 24 STRANDS MULTIMODE						FIOP-ST

& 12 STRANDS SINGLE MODE INDOOR/OUTDOOR CONSTRUCTION,

PDR CABLES ARE FLAME RATED AND SUITABLE FOR BOTH INDOOR

AND OUTDOOR INSTALLATIONS 0.539" O.D. MFG BERK-TEK,

P/N #PDR12B036024CB3510/15-012AB1010.

FIOPMM2		MULTI-FIBER, 2 FIBERS, FIBER IS MULTIMODE 62.5 MICRON

CORE, 125 MICRON CLADDING, 250 MICRON COATING, 900 MICRON

BUFFERING, MFR IS AT&T, 0.12 X 0.21" O.D. CODE #1816A,

COMCODE 103 910 170.

FIOPMM3		MULTI-FIBER, MULTIMODE 62.5 MICRON CORE, 125 MICRON

CLADDING, FDDI PLENUM DUPLEX (ZIPCORD). BY FIBER INSTRUMENT

SALES: PART#602-PT-ZC-62AFD.

FIOPMM12		MULTI-FIBER, 12 FIBERS, FIBER IS A MULTIMODE 62.5			1Y		FIOP-ST,FO-SPL

MICRON CORE, CABLE CORE IS 'LIGHTPACK' CABLE FILLED CORE.

SHEATH IS STEEL REINFORCED CROSSPLY, 0.42" O.D., MFR.

AT&T, PRODUCT CODE 3DAX-012, COMCODE 105 054 878.

SPECIAL NOTE:THIS CABLE IS TO BE TERMINATED BY QUALIFIED

PERSONNEL ONLY. CABLE AS INSTALLED FOR THE

SLC IS TERMINATED USING 'ST' TYPE CONNECTORS.

USE COLOR CODE TABLE 1Y.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

FIOPMM24		MULTI-FIBER, 24 FIBERS, FIBER IS A MULTIMODE 62.5			1Y		FIOP-ST,FO-SPL

MICRON CORE, CABLE CORE IS 'LIGHTPACK' CABLE FILLED CORE.

SHEATH IS RODENT-LIGHTING PROTECTED CROSSPLY, 0.42"

O.D., MFR. AT&T, PRODUCT CODE 3DHX-024, COMCODE

105 080 360. SPECIAL NOTE:THIS CABLE IS TO BE TERMINATED

BY QUALIFIED PERSONNEL ONLY. CABLE AS INSTALLED FOR THE

SLC IS TERMINATED USING 'ST' TYPE CONNECTORS.

USE COLOR CODE TABLE 1Y.

FIOPMM48		MULTI-FIBER, 48 FIBERS, FIBER IS A MULTIMODE 62.5			1Y		FIOP-ST, FO-SPL

MICRONCORE, CABLE CORE IS 'LIGHTPACK' CABLE FILLED CORE.

SHEATH IS  RODENT-LIGHTING PROTECTED CROSSPLY, 0.42"

O.D., MFR. AT&T, PRODUCT CODE 3DHX-048, COMCODE

105 080 480.

SPECIAL NOTE:THIS CABLE IS TO BE TERMINATED BY QUALIFIED

PERSONNEL ONLY. CABLE AS INSTALLED FOR THE

SLC IS TERMINATED USING 'ST' TYPE CONNECTORS.

USE COLOR CODE TABLE 1Y.

FIOPMM52		MULTI-FIBER, 52 FIBERS, FIBER IS A MULTIMODE 62.5			1Y		FIOP-ST, FO-SPL

MICRON CORE, CABLE CORE IS 'LIGHTPACK' CABLE FILLED CORE.

SHEATH IS RODENT-LIGHTING PROTECTED CROSSPLY, 0.42"

O.D., MFR. AT&T, PRODUCT CODE 3DHX-052, COMCODE

105 080 501.

SPECIAL NOTE:THIS CABLE IS TO BE TERMINATED BY QUALIFIED

PERSONNEL ONLY. CABLE AS INSTALLED FOR THE

SLC IS TERMINATED USING 'ST' TYPE CONNECTORS.

USE COLOR CODE TABLE 1Y.

FOMMDP62		FIBER OPTIC, 62.5/125UM, MULTIMODE, DUPLEX, LSZH.					LC-DUP

0.08” O.D.SUPPLIER: MANCO WIRE AND CABLE,

(510)632-3290. P/N: LSZH 2X 62.5/ 2MIL

FOPTMM12		CORNING 12 STRAND MULTIMODE FIBER TRUNK

P/N 012TWZ-T4131D2N 12 FIBER ALTOS LSZH GEL-FREE CABLE

JACKET 50UM PREMIUM ULTRA-BEND 7.5 10GBE UP TO

150 M 3.0/1.0 DB/KM 950 MHZ-KM EMB 12F/TUBE PRINT

IN FT WITH INDUSTRIAL PRINT kg/km (LB/1000ft) 91 (67),

NOMINAL OUTER DIAMETER mm (in)¹ 11.5 (0.46),

MINIMUM BEND RADIUS 11.5 (0.46).

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

FOSMLCDP		FIBER OPTIC, RISER RATED, SINGLE MODE JUMPER WITH

FACTORY INSTALLED LC DUPLEX STYLE CONNECTORS.

LENGTHS VARY DEPENDING ON THE UNIT PURCHASED.

TYPICAL P/N: SYSTIMAX FPCWLCUC01-R.

FO2RSMRO		(Fiber Optic cable, 2 Ribbon, Single Mode, Riser-rated, indoor / Outdoor)

Long Description for CAPTAR, (feel free to re-format for clarity as necessary):

24-STRAND, SINGLE-MODE, FIBER OPTIC RIBBON CABLE. INDOOR/OUTDOOR, RISER-RATED, (ONFR), GEL-FILLED.

CORNING PART NUMBER: 024ECF-14101-20

.46" (11.6MM) NOMINAL OD

6.9" (174MM) MINIMUM BEND RADIUS (INSTALLATION) 4.6" (116MM) MINIUMUM BEND RADIUS

(OPERATION) MAX TENSILE STRENGTH, SHORT-TERM: 600 LBF (2700N) MAX TENSILE STRENGTH,

LONG-TERM: 135 LBF (600N) WEIGHT: 109LB / 1000'

FO4RSMRO		(Fiber Optic cable, 4 Ribbon, Single Mode, Riser-rated, indoor / Outdoor)

Long Description for CAPTAR, (feel free to re-format for clarity as necessary):

48-STRAND, SINGLE-MODE, FIBER OPTIC RIBBON CABLE. INDOOR/OUTDOOR, RISER-RATED, (ONFR), GEL-FILLED.

CORNING PART NUMBER: 048ECF-14101-20

.46" (11.6MM) NOMINAL OD

6.9" (174MM) MINIMUM BEND RADIUS (INSTALLATION) 4.6" (116MM) MINIUMUM BEND RADIUS (OPERATION)

MAX TENSILE STRENGTH, SHORT-TERM: 600 LBF (2700N) MAX TENSILE STRENGTH,

LONG-TERM: 135 LBF (600N) WEIGHT: 109LB / 1000'

FO6RSMRO		(Fiber Optic cable, 6 Ribbon, Single Mode, Riser-rated, indoor / Outdoor)

Long Description for CAPTAR, (feel free to re-format for clarity as necessary):

72-STRAND, SINGLE-MODE, FIBER OPTIC RIBBON CABLE. INDOOR/OUTDOOR, RISER-RATED, (ONFR), GEL-FILLED.

CORNING PART NUMBER: 072ECF-14101-20

.51" (12.7MM) NOMINAL OD

7.5" (191MM) MINIMUM BEND RADIUS (INSTALLATION) 5" (127MM) MINIUMUM BEND RADIUS (OPERATION)

MAX TENSILE STRENGTH, SHORT-TERM: 600 LBF (2700N) MAX TENSILE STRENGTH, LONG-TERM: 135 LBF (600N)

WEIGHT: 117LB / 1000'

FRG59R		SAME CABLE AS RG59R, INSTALLED IN 1/2" ALUMINUM

FLEX CONDUIT FOR ADDED PROTECTION. THIS IS NORMALLY

SPECIFIED AS PART OF A PRE-FABRICATED CABLE ASSEMBLY.

GP330HF		GRANVILLE PHILLIPS, FLEXIBLE CABLE FOR VACUUM. ONE

END IS PRE-WIRED WITH A SPECIAL CONNECTOR, BNC AND AMP4P;

AND THE OTHER END IS PRE-WIRED WITH AN IPI MODEL 9237

CONNECTOR. 0.4" O.D.

HABIA			SIXTY CONDUCTOR, #XX AWG, HV CABLE, FURTHER INFO

PENDING, 1.140" O.D., MFG HABIA P/N 98 W 04.

HC30A			CIRCULAR MULTICONDUCTOR. 20 CONDUCTORS AND 3 COAX CABLES.

0.275" O.D. MFR: CIDTEC.

HD15MF		PRE-FABRICATED COMPUTER CABLE HD-SUB 15 PIN MALE TO FEMALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPLLIERS, IE. "Black Box Corp."

HP-CORD		HP POWER METER CORD. PRE-WIRED WITH SIX PIN						HPJ, HPP

CONNECTORS ON EACH END. ONE END HAS A FEMALE

CONNECTOR, HPJ, ON IT AND THE OTHER END HAS A MALE

CONNECTOR, HPP, ON IT.

HV-CJ			COAXIAL CONNECTOR, MALE, 10KV HV CABLE JACK.

REYNOLDS CAT. NO. 1679096-C

HV-SENS		TRI-AXIAL, SENSOR CABLE, SHIELDED, LSNH, TRAY RATED

HIGH VOLTAGE (3KV) FOR SENSOR, FAST SHUTTER.USED ON VAT

EQUIPMENT/SYSTEM. CONTACT/ORDER INFORMATION: VAT AG,

(925) 944-3570. PART NUMBER: 770CS-99L(X) (X IS LENGTH

IN METERS), THE CABLE(S) WILL BE SUPPLIED BY THE VENDOR

CUSTOM MADE TO LENGTH WITH CONNECTORS ALREADY ATTACHED.

HVSPEC1		SPECIAL HIGH VOLTAGE CABLE, #6 AWG COPPER, 120KV DC					HV220, LR6#10

HVK DPS CABLE, KERITE CAT-# 1985, 1.19" O.D., 80 MILS PVC

JACKET.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

HVSPEC2		SPECIAL HIGH VOLTAGE CABLE, THIS CABLE CONSISTS OF					LSY#8, MS5S

ONE 3KV AC MIL RATED HOOK-UP WIRE, #12AWG, ANIXTER NO.

MIL6878/3-BLE-RED AND ONE 3KV AC MIL RATED HOOK-UP WIRE,

#12AWG, ANIXTER NO. MIL6878/3-BLE-WHITE. THESE TWO WIRES

ARE TO BE INSTALLED IN 1/2" FLEX CONDUIT. 0.875" O.D.

IG-CABLE		PREWIRED CABLE ASSEMBLY WITH BOTH A MALE AND A						GP-GAU, VG-CON,

BNC CONNECTOR AT ONE END FOR CONNECTION TO EITHER A					VGAUGE

GRANVILLE-PHILLIPS SERIES 270 ION-GAUGE CONTROLLER, OR A

VACUUM GAUGE DROP BOX (WHICH USAGE IS DETERMINED BY

THE DESIGNATED TERMINATION), 0.375" O.D.

NOTE THAT THIS ASSEMBLY MAY BE PRE-FABRICATED USING

TYPE 'ION-GAU' CABLE.

ION-GAU		SPECIAL LLL ION GAUGE CABLE. ONE UNSHIELDED,						IG21, IG22

TWISTED PAIR OF #14 AWG, TINNED-COPPER CONDUCTORS, TWO

#16 AWG, TINNED-COPPER CONDUCTORS, EACH INDIVIDUALLY

SHIELDED WITH BRAID SHIELDS. THE INSULATION IS RATED AT

GREATER THAN 1000 MEGOHMS PER FOOT OF CABLE. 0.38"

O.D., LRL SPEC. LLL-6145-24464.

ION-GAU2		SPECIAL ION GAUGE CABLE. THREE #12 AWG WIRES,						AMP14P, IG-RS4

TWISTED TOGETHER WITH A FOIL OVERALL SHIELD AND 1 EA #22

AWG DRAIN WIRE. ONE COAX BELDEN #9311) LAYED IN PARALLEL.

ALL INSULATION USED IS PVC, 600V,. 0.550" O.D. THE MFR. IS

ANIXTER. PART NUMBER UNKNOWN.

ION-GAU3		SPECIAL ION GAUGE CABLE, CUSTOM COMBINATION. COAX (RG58) AND			IG23, IG24

MULTICONDUCTOR OVERALL SHIELDED WITH 22GA DRAIN WIRE.

MANUFACTURED BY COAST WIRE AND PLASTIC TECH., INC.

CARSON, CA PN# 02-0144

KAPTON		MINIATURE COAXIAL CABLE, KAPTON (POLYIMIDE) INSULATION,				BNCKAP, MCX

RADIATION RESISTANT, 0.94" O.D. CUSTOM MADE BY W.L. GORE

FOR CAPACITEC, INC.

LLNLSUP		LLNL (LAWRENCE LIVERMORE NATIONAL LAB) SUPPLIED CABLE

ASSEMBLY. THIS CUSTOM BUILT CABLE IS PROVIDED BY LLNL.

THIS CABLE ASSEMBLY IS SPECIFICALLY DESIGNED FOR USE ON

LLNL EQUIPMENT.O.D.(OUTSIDE DIAMETER) WILL VARY BASED ON

DESIGN AND MATERIAL BEING USED.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

LMR195FR		COAX CABLE, 50 OHM,  CAPACITANCE  25.4 PF/FT,

FLEXIBLE LOW LOSS,LOW SMOKE ZERO HALOGEN, TYPE

CMR OR CATVR (OKAY TO BE USED IN CABLE TRAYS

PER NEC ARTICLE 820.154 (D)(E). 0.195 IN. O.D.

MFR: TIMES MICROWAVE, P/N: LMR-195-FR.

LMR200X2		COAXIAL CABLE, 50 OHMS, 0.195" O.D.,0.022LB/FT						N200, N200BJ

TIMES MICROWAVE SYSTEMS OR EQUIVALENT. NOMINAL VELOCITY 83%.

CAT. #LMR200.

LMR200FR		COAXIAL CABLE, 50 OHMS, 0.195” O.D., CMR/MPR (PCC-FT4)				N200,N200BJ

NON-HALOGEN, 0.022LB/FT.TIMES MICROWAVE SYSTEMS OR

EQUIVALENT.  NOMINAL VELOCITY 83%.  CAT. #LMR-200-FR.

LMR240X2		COAXIAL CABLE, 50 OHMS, 0.240" O.D.,0.034LB/FT.						N240, N240BJ

TIMES MICROWAVE SYSTEMS OR EQUIVALENT. NOMINAL VELOCITY 84%

CAT. #LMR-240.

LMR240FR		COAXIAL CABLE, 50 OHMS. 0.240" O.D., CMR/MPR (PCC-FT4)				N240, N240BJ,BNC240

NON-HALOGEN, 0.034LB/FT. TIMES MICROWAVE SYSTEMS OR SPECIAL

EQUIVALENT. NOMINAL VELOCITY 84%. CAT.#LMR-240-FR.

LMR2FRX4		SET OF 4 EACH LMR240FR CABLES, TIMED, MATCHED AND LABELED				N240, N240BJ

FOR BEAM POSITION MONITORS. TREATED AS A SINGLE CABLE.

LMR400X2		COAXIAL CABLE, 50 OHMS, 0.405" O.D.,0.068LB/FT						N400, N400BJ

LMR400X4		TIMES MICROWAVE SYSTEMS OR EQUIVALENT. NOMINAL VELOCITY 85%,

CAT. #LMR400.

LMR400FR		COAXIAL CABLE, 50 OHMS, 0.405" O.D., CMR/MPR (PCC-FT4)				N400, N400BJ

NON-HALOGEN, 0.068LB/FT, TIMES MICROWAVE SYSTEMS OR

EQIVALENT. NOMINAL VELOCITY 85%. CAT. #LMR-400-FR

LMR4FRX4		SET OF 4 EACH LMR400FR COAXIAL CABLES, TIMED, MATCHED AND				N400, N400BJ

LABELED FOR BEAM POSITION MONITORS. TREATED AS A

SINGLE CABLE. OD EA CABLE = 0.405”; ODT= 1.296”.

LMR600		COAXIAL CABLE, 50.0 OHMS, 0.590" O.D., TIMES 						NM-L600, NF-L600

FREQUENCY @ 2.5 GHZ, TEMPERATURE RANGE -40C TO +85C

NOMINAL VELOCITY OF PROPAGATION 87% ZCOMAX TECHNOLOGIES

#LMR600.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

LMR600FR		COAXIAL CABLE, 50 OHMS, 0.590” O.D., CMR/MPR (PCC-FT4)				N600, N600BJ

NON-HALOGEN, 0.131LB/FT. TIMES MICROWAVE SYSTEMS

OR EQUIVALENT.NOMINAL VELOCITY 87%. CAT.#LMR-600-FR.

LMR6FRX4		SET OF 4 EACH LMR600FR CABLES, TIMED, MATCHED AND					N600, N600BJ

LABELED FOR BEAM POSITION MONITORS. TREATED AS A SINGLE CABLE.

NMRI/O		STRAND OF 6-0.14MM SQ. TINNED COPPER EXTRA FLEXIBLE

CONDUCTORS INSULATED POLYMER TWISTED UNDER A POLYESTER

TAPE AND COAXIAL(RG318) WITH STRANDED TINNED COPPER

CONDUCTOR, 0.12MM TINNED COPPER BRAID INSULATION AND PVC

JACKET FLAT CABLE. 250V, 7.5-0.3X5-0.3MM O.D. MULLER

SA CAT.#26512/A.

NOKIA			THREE TWISTED PAIR, #28 AWG, SOLID CONDUCTORS, ZERO

HALOGEN, CERN SPEC #23, TYPE MB06P IEC 332-1. 0.138" O.D.,

MFG. NOKIA KABEL.

NPMM10		CUSTOM MOTION ELECTRONICS ITEM, CUSTOM INTERCONNECT CABLE;

STANDARD FEATURES: MMCABLE CONSTRUCTION, MATERIALS; SPECIAL

FEATURES; 3QM LENGTH; NOTE: INCREASED CABLE LENGTH BEYOND

10M IS NOT RECOMMENDED. USER ASSUMES RESPONSIBILITY FOR LOSS

OF PRODUCT PERFORMANCE DUE TO SIGNAL DEGRADATION.

MUST BE USED WITH MMCABLE-REG MODEL # 10SI40097,

NEWPORT EXPERIENCE/SOLUTIONS

NPMM30		CUSTOM MOTION ELECTRONICS ITEM, CUSTOM INTERCONNECT CABLE;

STANDARD FEATURES: MMCABLE CONSTRUCTION, MATERIALS; SPECIAL

FEATURES; 3QM LENGTH; NOTE: INCREASED CABLE LENGTH BEYOND 10M

IS NOT RECOMMENDED. USER ASSUMES RESPONSIBILITY FOR LOSS OF

PRODUCT PERFORMANCE DUE TO SIGNAL DEGRADATION. MUST BE USED

WITH MMCABLE-REG MODEL # 10SI40097,

NEWPORT EXPERIENCE/SOLUTIONS

PREFAB		CABLE AND CONNECTOR DETAILS ARE PROVIDED BY OUTSIDE VENDOR.

R4010			HIGH VOLTAGE SILICONE LEAD WIRE, UL3239 STYLE, #10 AWG,				SOLDER, LRY-8

40KVDC, O.360" O.D., ROWE INDUSTRIES CAT. #R800-4010.

RADIONET		TWIN LEAD TV CABLE & RADIO CABLE, CELLULINE 300						SOLDER

OHMS, 0.300"X0.400" O.D., BELDEN CAT.#8275.

RG6			COAXIAL CABLE, 75 OHMS, COPPER CENTER WITH SILVER COATING.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

RG6-QF		COAXIAL CABLE, 75OHMS COPPER CENTER CONDUCTOR, QUAD SHIELDED,			RG-6QS

EXTRA-FLEXIBLE ANIXTER PN# 1362A

RG6U-CN		Coaxial cable, 75 Ohms, 18awg center copper conductor

.40 in., Gas injected FHDPE, shielded, .274 in. OD,

LSZH jacket, weight 42.9lbs/1000ft,UL1685, UL444,

FT4 loading,RoHS compliant, Non plenum rated, CMG-LS,

max pulling tension 69lbs. For RG6 Control-Net.

RG8			COAXIAL CABLE, RG8/U, 50 OHMS, 0.405" O.D., MIL-C-17D,				N213, BNC213

BELDEN CAT. #9251, OR ANDREW CAT. #24153.FOAM DIELECTRIC,

OUTER CONDUCTOR IS 100% FOIL, 88% BRAID.

RG8A			COAXIAL CABLE, RG8/U, 50 OHMS, DOUBLE SHIELDED, 0.405"				N8-A

O.D., ANDREW CAT. #241543.

RG11A			COAXIAL CABLE, RG-11A/U, 0.405" O.D., 75 OHMS, MIL-C-17D,				N11

BELDEN CAT. #8261.

RG11TRI		TRIAXIAL CABLE, SIMILAR TO RG-11/U, CELLULAR						N11, N213

POLYETHYLENE INSULATION, BLACK JACKET, 0.475" O.D., 75

OHMS, BELDEN CAT. #8233.

RG22			TWINAXIAL CABLE, RG-22A/U, 0.42" O.D., 95 OHMS.						TX22

SLAC S/N61-329-006-01.

RG58			COAXIAL CABLE, RG-58C/U, 50 OHMS, 0.195" O.D., MIL-C-17G,				BNC58, TNC58

BLACK NON-CONTAMINATING PVC JACKET.

BELDEN CAT. #8262. 61-329-000-07.

RG58PLEN		COAXIAL CABLE, RG58/U, PLENUM, 50 OHMS, FOIL AND					9907

BRAID SHIELDS, 0.165" O.D., BELDEN CAT #89907

RG58R			COAXIAL CABLE, RG58A/U OR RG58C/U, 50 OHMS, MIL-C-17D,				SHV58,HV58

0.195"O.D., RED JACKET, 2.5KV MAX., SLAC S/N61-329-007-01.

RG58TR		COAXIAL CABLE, RG58/U, TRAY RATED, 53.5 OHM, .159"

O.D., TEFLON JACKET, ANIXTER/BELDEN #88240.

RG58TLN		COAXIAL CABLE, 50 OHMS,0.235" O.D., XLPE JACKET,

PE DIALECTRIC, NON-HALOGEN, TIMES MICROWAVE SYSTEMS

CAT.# LSSB-RG58, PART # 43030 M17/183-00001

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

RG59			COAXIAL CABLE, RG59/U OR RG59B/U, 0.242" O.D., 73 OR					BNC59, F59B

75 OHMS MIL SPEC. MIL-C-17D. SLAC S/N 61-329-000-02.					FIXED

RG59DS		COAX RG59/U DBL CU BRAID.

RG59QS		COAXIAL CABLE, HEADEND RG59/U, QUAD SHIELDED,						F59QS, F59DS

0.262" O.D., TIMES FIBER COMMUNICATIONS INC.CAT # 4224OV.

RG59R			COAXIAL CABLE, RG59/U OR RG59B/U, RED JACKET, MIL-C-17D,

75 OHMS, 3.0KV MAX. SLAC S/N61-329-007-02.						SHV59J, SHV59P

RG59TLN		COAXIAL CABLE, 75 OHMS, 0.237" O.D., XLPE JACKET,

PE DIALECTRIC, NON-HALOGEN, LIBERTY CABLE CAT. #

RG59-SD-HF-WHT

RG62			COAXIAL CABLE, RG-62/U, 0.242" O.D., 93 OHMS.						BNC62

SLAC S/N61-329-000-13.

RG108A		TWINAXIAL CABLE, RG-108A/U, 0.24" O.D.,78 OHMS.						LEMO2P, TX108

RG108TLN		Anixter P/N M17/186-00001  75 Ohm Nominal Impedence LSNH – Low Smoke Non Halogen

2C-.0378 STR TNC PE TNC BRD SHD CLP LS RG108 78 OHM**QPL/CTR  Weight = 61lb per 1000ft,

Overall Diameter = .235

RG142B/U		SMA MALE TO TYPE N MALE, 24" IN LENGTH, P/N

RG142-SMAN-NM-24 SMA MALE TO SMA MALE, 24" IN LENGTH,

P/N RG142-SMAN-SMAN-24. VENDOR:APPLIED SPECIALTIES,

(408) 370-2644, CAMPBELL CALIFORNIA.

RG142SNV		SMA MALE TO TYPE N MALE, 50 OHM, RG142B/U DOUBLE SHIELDED

VENDOR PATCH CABLE.SUGGESTED VENDOR-PATERNACK ENTERPRISES.

PASTERNACK No'S PE3568FL-12, PE3568FL-24, PE3568FL-36,

PE3568FL-48, PE3568FL-60,PE3568FL-72, XX (CUSTOM LENGTH),

WHERE THE LAST TWO DIGITS INDICATE STANDARD LENGTHS IN

INCHES.

RG174			COAXIAL CABLE, RG174/U, 0.100" O.D. 50 OHMS, MIL-C-17F,				LEMO

SLAC S/N61-329-000-19.

RG174TLN		COAXIAL CABLE, RG174, 0.110" O.D. 50 OHMS, LOW SMOKE ZERO HALOGEN,

PART NUMBER: M17/196-00001.

RG188U		SPECIAL CABLE MADE OF TYPE RG-188U COAX, 50 OHMS.

10 INDIVIDUAL PIECES WITH THE BRAIDED OUTER CONDUCTORS

CONNECTED TOGETHER ON EACH END AND BROUGHT OUT ON

PIN "L". SLAC S/N 61-329-000-16

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

RG213			COAXIAL CABLE, RG-213/U, BLACK OR GREEN JACKET, 0.405"

O.D., 50 OHMS, MIL SPEC. MIL-C-17F. SLAC S/N61-329-000-06.

RG213R		SAME AS RG213 EXCEPT:  RED JACKET, NO SLAC S/N, 7.0KV					HV213,ILP1,ILP2

MAX.,	0.405" O.D., ORDERED FROM MANCO.							MS-HVS, HN213

RG214			COAXIAL CABLE, RG-214/U, 0.425" O.D., 50 OHMS, MIL-SPEC.				N214, HN214

MIL-C-17F. SLAC S/N61-329-000-10.								BNC214, HV213,

BBJ214, N214JB

RG214TLN		COAXIAL CABLE, 50 OHMS, 0.425" O.D., XLPE JACKET,

PE DIALECTRIC,NON-HALOGEN, TIMES MICROWAVE SYSTEMS

CAT.# LSSB-RG214 PART # 43038 M17/190-00001

RG214X4		SPECIAL SET OF 4 EACH RG-214/U COAXIAL CABLES, TIMED,					N214

MATCHED, AND LABELED FOR BEAM POSITION MONITORS.

TREATED AS A SINGLE CABLE.

RG218R		COAXIAL CABLE, RG-218/U, RED JACKET, 0.87" O.D., 50					N218

OHMS MIL-SPEC. MIL-C-17D.

RG220			COAXIAL CABLE, RG-220/U, 1.12" O.D., 50 OHMS, MIL-SPEC.				HV220

MIL-C-17D.

RG223			COAXIAL CABLE, RG-223/U, 0.216" O.D., 50 OHMS, MIL-SPEC.				BNC223, TNC223

MIL-C-17D.												N223, SMR223

RG223X4		SPECIAL SET OF 4 EACH RG-223/U COAXIAL CABLES, TIMED,					SMA223, SMR223

MATCHED, AND LABELED FOR BEAM POSITION MONITORS.					N223

TREATED AS A SINGLE CABLE. 0.432" O.D.

RG223X6		SPECIAL SET OF 6 EACH RG-223/u COAXIAL CABLES TIMED,					SMA223

MATCHED AND LABELED FOR BEAM POSITION MONITORS.

TREATED AS A SINGLE CABLE. 1.296" O.D.

RS232-10		10 LINE COMPUTER COMMUNICATION CABLE WITH 25

POSITION "D" CONNECTORS ON EACH END. MFR. INMAC

RWB			A SET OF 3 RADIATION RESISTANT WIRES CONSISTING OF ONE

EACH OF THE FOLLOWING: #20AWG-RED, #16AWG-WHT, #18AWG-

BLK. XML-125 SERIES, 600V.

SPECCBL		EMI PART#15-955-010.6 CONDUCTORS.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

T/C			THERMOCOUPLE, #16 TW SH. MFR: OMEGA#EXPP-K-16.

THICKNET		ETHERNET COAXIAL CABLE, YELLOW PVC JACKET, CL2						N213

RATED, 0.405" 0.D., BELDEN CAT. #9880.

THRM-CU	3 CONDUCTOR, THERMOCOUPLE EXTENSION WIRE, TYPE CU, 					STRIP

26 AWG STRANDED. 0.07” O.D. WIRE INSULATION AND

OVERALL JACKET:GLASS BRAID. RED (NEGATIVE) AND BLACK

(POSITIVE)MFG: OMEGA. P/N: EXGG-3CU-26S.

CABLE TRAY APPLICATION: WHEN ROUTING THIS THEMOCOUPLE WIRE

IN A CABLE TRAY, PROTECT THE WIREOR WIRES USING INNERDUCT

TUBING, MFG: SUPERFLEX, FLEXIBLE SPLIT TUBING

(GRAY – FLAME RETARDANT), ITEM #125-XXXXG.

THRM4CU		4 CONDUCTOR, RTD, TYPE CU, 									STRIP

26 AWG STRANDED. 0.07" O.D. WIRE INSULATION AND OVERALL JACKET:

GLASS BRAID. RED (NEGATIVE) AND  BLACK (POSITIVE)

MFG: OMEGA. P/N: EXGG-4CU-26S.

CABLE TRAY APPLICATION: WHEN ROUTING THIS THERMOCOUPLE WIRE

IN A CABLE TRAY, PROTECT THE WIRE OR WIRES USING INNERDUCT

TUBING, MFG: SUPERFLEX, FLEXIBLE SPLIT TUBING

(GRAY – FLAME RETARDANT), ITEM #125-XXXXG.

TIMES			COAXIAL CABLE, RED JACKET, 7.5KVDC, 26 OHMS, 0.195"					HV-C, IPVB

O.D., RADIATION ENVIRONMENT RATING 250 MEGARADS, MFR.

TIMES MICROWAVE SYSTEMS, P/N AA-7406, CODE IDENTIFICATION

#68999. SLAC S/N61-329-007-10.

TMS8481		COAXIAL CABLE, TIMES MICROWAVE, #8481, .0533

O.D.", 22.5 OHMS, BARE COPPER CTR CONDUCTOR, MIL-C-17.

TWC-78-1		TWINAX CABLE, 78 OHMS, 0.150" O.D., 8 TWISTS PER					155-9, 75-29

FOOT, TROMPETER CAT.#TWC-78-1, CABLE GROUP 29.

TWC-78-2		TWINAX CABLE, 78 OHMS, 0.242" O.D., 4 TWISTS PER					75-9

FOOT, TROMPETER CAT.#TWC-78-2, CABLE GROUP 9. BLUE JACKET.

TWC-78FR	   TWIN CONDUCTOR 78 OHM, 20AWG, COAXIAL CABLE, LSZH (ZEROHAL)		     BNC-TWN, 75-9

JACKET, 90% MIN. SHIELD, 18.8 PF/FT, .243 O.D.,(LONG LEAD TIME:

CHEMINAX P/N 7820D0831) P/N: M17-186-00001.

TWC100FR		TWINAX CABLE, 100 OHMS, .330" OD, 300V RMS, 100% FOIL + 85% TC BRAID SHIELD.

BELDEN SPECIAL ORDER, PART# 9207-LSZH.

See color		TERM.TYPE

CABLE TYPE		CABLE DESCRIPTION								CODE TABLE		(See Table 3)

TWC9207N	   TWINAX CABLE, ONE PAIR, #20AWG, STRANDED(7X28),				    TX227241

TINNED COPPERCONDUCTOR, POLYETHYLENE INNER JACKET,

DUFOIL, ALUMINUM SHIELD 85% TINNED COPPER BRAID,

LSNH JACKET,.34" O.D.,300 VOLT, BELDEN CAT# 9207NH.

TWC-9272		TWINAX CABLE, ONE PAIR, #20 AWG, TINNED COPPER, 93% SHIELD				42-36

COVERAGE, .244" O.D.,300 VOLT, BELDEN CAT. # 9272.

TWC-9860		TWINAX CABLE, ONE PAIR, #16 AWG, BARE COPPER, 100% SHIELD				75-46

COVERAGE, 124 ohm, .440" O.D., 30 VOLT, BELDEN CAT. #9860

TYPE-C		COAXIAL CABLE, TYPE-C,31 OHM, DIA. 0.195" O.D.,						HV58, SHV-C, HV58J

REYNOLDS INDUSTRIES # 167-2669, PE JACKET, PE DIALECTRIC,

COAXIAL HIGH VOLTAGE STORES ID # 088412

UPS-1400		SMART UPS SIGNALLING RS-232 CABLE,APC SMART-UPS,					DB9

PART NUMBER: SU1400RM2U, AC OVT: 6 ACP

VAC-HV		COAXIAL CABLE, VACUUM-HV CABLE, 31 OHM-MAYBE, DIA. 0.5” O.D. A GUESS

GAMMA VACUUM # NO PART NUMBER AT THIS TIME, LSZH, COAXIAL

HIGH VOLTAGE CABLE.

VARIAN		VARIAN UNARMORED, FLEXIBLE CABLE FOR ION PUMPS.						IPA, IPVA

ONE END IS PRE-WIRED WITH A SPECIAL CONNECTOR, IPVA,

AND THE OTHER END IS PRE-WIRED WITH AN AMPHENOL

CONNECTOR, IPA. 0.4" O.D.

VARIAN-A		VARIAN STAINLESS STEEL, ARMORED, FLEXIBLE CABLE						IPL3, IPVA

FOR ION PUMPS. ONE END IS PRE-WIRED WITH A SPECIAL

CONNECTOR, IPVA. THE OTHER END SHOULD BE PREPARED FOR AN

IPL3 TERMINATION. 0.4" O.D.

VSAM			CONSISTS OF TWO 37C24TEF CABLES. EACH CABLE IS

EIGHTEEN PAIRS WITH A DRAIN WIRE, #24AWG TINNED

COPPER, FOAM INSULATED, OVERALL BELDFOIL ALUMINUM-

POLYESTER SHIELD, 0.484" O.D. BELDEN P/N 88118.

FOR NON PLENUM APPLICATIONS USE TWO 18PR22OS CABLES.

FOR PIN DETAILS CONTACT P.J. STILES. No DRAWING

NUMBER ASSIGNED AT THIS TIME.

WCC			WATER COOLED CABLE, 1" AL.

WCC-1			WATER COOLED CABLE, 1/2" COPPER.

WPMCOAX		COAXIAL CABLE 50ohm Max. Frequency 7.5GHz, Foamed 					N-50UV

polyethylene,halogen free, 12.9mm O.D.,Min Bend radius

129mm, Man. P/N HUBER+SUHNER S 10172 B-11 50 Ohm,

Weight 15 kg/100meters, temp range -40C +85C

YR44731		PROFIBUS DP NETWORKING CABLE, 22 AWG, 1 TWISTED PAIR,

OVERALL SHIELD, LSZH JACKET, 52.5 OHM/KM, OD 0.315 IN,

56LBS/1000FT. BELDEN YR44731 600V.

### Table 3 - Cable Termination Descriptions

TOOLING NOTE:  Unless otherwise specified, the tooling specified below is as follows:

a. Crimp LUG tools are AMP.

b. MS series and other multi-pin connector tools are BURNDY.

c. Coaxial cable trim and crimp tools are KINGS.

---------------------------------------------------------------------------------------------------------------------

TERMINAL PLUG CODES:

T (P,C)(A,B…H)xx(A,B,C,D)(A,B,C,D)(N,S,L,D,P)

Terminal Plug Codes Definition:

_ Power, Control

_ (Pitch) A- 2.5MM, B- 3.5, C- 3.81, D- 5.0 E- 5.08, F- 7.5, G- 7.62, H- 10.16

_  xx (# of Position)

_ (Wire Entry) A- Top, B- Left Side, C- Right Side, D- 45 Degrees

_ (Termination Type) A- Screw Top, B- Screw Side, C- Fast Connect, D- Spring Cage

_ (Flange) None, Screw, Self Locking, Direct Mounting, Panel Mount

----------------------------------------------------------------------------------------------------------------------

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

42-36			TWINAX CONNECTOR, PASTERNACK PE 4236							TWC-9272

75-9			TWINAX CONNECTOR, CABLE PLUG, TROMPETER CAT.#PL75-9 FOR	VME CRATES		TWC-78-2

CABLE GROUP 9

75-29			TWINAX CONNECTOR, CABLE PLUG, TROMPETER CAT #PL75-29		VME CRATES		TWC-78-1

FOR CABLE GROUP 29

75-46			TWINAX CONNECTOR TROMPETER TEI-14949, CAT.#PL75-46					TWC-9860

155-29		TWINAX CONNECTOR, CABLE PLUG, TROMPETER CAT #PL155-29,				TWC-78-1

FOR CABLE GROUP 29.

972411P		THE CONNECTOR IS FORMERLY, MIL-C-5015 NOW 97 SERIES

PART NO. 97-3106A-24-11P AS WELL AS 97-3106A-24-11S

9 CONTACT CONNECTOR 6 #12AWG AND 3 #8AWG WIRES,OLIVE

DRAB METAL SHELL.

972411S		THE CONNECTOR IS FORMERLY, MIL-C-5015 NOW 97 SERIES

PART NO. 97-3106A-24-11P AS WELL AS 97-3106A-24-11S

9 CONTACT CONNECTOR 6 #12AWG AND 3 #8AWG WIRES,OLIVE

DRAB METAL SHELL.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

9907			COAXIAL CONNECTOR, BNC CABLE PLUG, BNC9907HPC, AMP		THINNET		RG58PLEN

P/N 2-221128-7 USE AMP CRIMPING TOOL 58433-2

WITH DIE 58436-1.

3M16S			SIXTEEN PIN CONNECTOR, FEMALE FLAT RIBBON CABLE PLUG,

POLARIZING SLOTS, 3M P/N #3452-6600,NEWARK CAT.#46F4657.

3M20S			TWENTY PIN CONNECTOR, FEMALE FLAT RIBBON CABLE PLUG,

POLARIZING SLOTS, 3M P/N#3421-6000 NEWARK CAT.P/N#46F8438.

3M40S			FORTY PIN CONNECTOR, FEMALE FLAT CABLE PLUG, 3M CAT.					40C24OS

#3417-6640, SLAC S/N59-299-165-40.

3M50S			FIFTY PIN CONNECTOR, FEMALE FLAT CABLE PLUG.

16FERLS		SINGLE INSULATED WIRE FERRULES CONNECTOR, 16AWG

MANUFACTURER ABB INC.P/N 30445703.

16FERLT		TWIN INSULATED WIRE FERRULES CONNECTOR, 16AWG

MANUFACTURER ABB INC.P/N 30456305.

18FERLS		SINGLE INSULATED WIRE FERRULES CONNECTOR, 18AWG

MANUFACTURER ABB INC.P/N 30445602.

18FERLT		TWIN INSULATED WIRE FERRULES CONNECTOR, 18AWG

MANUFACTURER ABB INC.P/N 30456103.

20FERLS		SINGLE INSULATED WIRE FERRULES CONNECTOR, 20AWG

MANUFACTURER ABB INC.P/N 30445501.

20FERLT		TWIN INSULATED WIRE FERRULES CONNECTOR, 20AWG

MANUFACTURER ABB INC.P/N 30455911.

500MCSI		MULTI-CONTACT SOCKET WITH BAYONET LOCKING AND CRIMP SLEEVE,				500TLSNH

P/N KBT16BV-NS/M50-240. USE CRIMP TOOL ELPRESS P/N V1311C

WITH DIE 13CB30. NOTE: CONNECTORS ARE ALL THE SAME. ORDER

APPROPRIATE FERREL AND NUT FOR WIRE TYPE AND SIZE OTHER

THAN 500TLSNH.

535MCS		SLEEVE, CRIMP, MULTI-CONTACT P/N H240N/M20, WITH MODIFIED	SPPS CHICANE BEND

THREADED SOCKET P/N B25N. USE CRIMP TOOL ELPRESS P/N

V 1311C WITH 13CB30 DIE SET.SECURE SLEEVE TO SOCKET,

TIGHTEN TO 12 FT/LBS OR 52NM. COVER SOCKET/SLEEVE AND

3 1/2" OF CABLE WITH HEAT SHRINK TUBING THOMAS & BETTS

P/N HS500-1000. "DO NOT USE WITH NEW INSTALLATIONS".

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

AC-BMP		BUSINESS MACHINE PLUG. AC POWER LINE CONNECTOR,			AC SERVICE

10AMP,250V, APPLIANCE INLET, STRAIGHT ENTRY, SCHURTER,

MALE CONNECTOR.

AC-BMS		BUSINESS MACHINE PLUG. AC POWER LINE CONNECTOR,10AMP,		AC SERVICE

250V, APPLIANCE INLET, STRAIGHT ENTRY, FEMALE CONNECTOR.

ACJBX			120VAC JUNCTION BOX WITH 1 OR 2 ACR CONNECTORS.			AC SERVICE		3C16/3V, 3C16FLX

ACM20P		   AC POWER PLUG, 208V, 20 AMPS, 3 PHASE, 4 WIRE.

DECONTACTOR (RATED TO BE DISCONNECTED WITH

POWER STILL ON IF NECESSARY),

LOTO (LOCKOUT TAGOUT SAFETY FEATURE),

MFG: MELTRIC CORPORATION, MFG SERIES: DSN20,

MFG P/N:63-18163.

SEE MELTRIC CATALOGUE FOR OTHER ACCESSORIES.

ACM60P		   AC POWER PLUG, 208V, 60 AMPS, 3 PHASE, 4 WIRE.

DECONTACTOR (RATED TO BE DISCONNECTED WITH

POWER STILL ON IF NECESSARY),

LOTO (LOCKOUT TAGOUT SAFETY FEATURE),

MFG: MELTRIC CORPORATION, MFG SERIES: DSN60,

MFG P/N:63-68163.

SEE MELTRIC CATALOGUE FOR OTHER ACCESSORIES.

ACP			AC MALE CONNECTOR, 3 WIRE, 15A, PARALLEL UGRD,			AC SERVICE		3C16/3V, 3C16FLX

NEMA 5-15P, HUBBEL 5266C, SLAC P/N58-299-202-07.					3C14FLX

ACP20			AC POWER CONNECTOR, 120/208V, 20 AMPS, 4 POLE, 5 WIRE					4C8TYR

GROUNDING, 3 PHASE Y, NEMA #L21-20R, MFR. HUBBELL,

CAT-# 2513 OR EQUIVALENT.

ACP22			AC POWER PLUG, TWIST-LOCK, 480V, 30 AMPS, 4 POLE, 5 WIRE

GROUNDING, 3 PHASE Y, NEMA #L22-30P, MFR. HUBBELL,

CAT-# 2821 OR EQUIVALENT.

ACR			AC FEMALE CONNECTOR, RECEPTACLE BODY, 3 WIRE, 20A IT SLOT, 	AC SERVICE		3C14FLX, 3C16FLX

HUBBEL 5369C, NEMA 5-20R, SLAC P/N 58-299-403-10.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

AMP4P			FOUR PIN CONNECTOR, MALE CIRCULAR PLUG, SHELL SIZE 11-4,				2PR22OS

AMP CAT. #206429-1,BACK SHELL, AMP CAT. #206062-3. USE THE

FOLLOWING PINS AS APPROPRIATE. USE CRIMPING TOOL AMP CAT.

#90277-1.

16-18 AWG AMP CAT. #66099-3

20-22 AWG AMP CAT. #66400-3

24-26 AWG AMP CAT. #66107-3

AMP4S			FOUR PIN CONNECTOR, FEMALE CIRCULAR PLUG, SHELL SIZE 11-4,				2PR22OS

AMP CAT. #206060-1, BACK SHELL AMP CAT. #206062-3. USE THE

FOLLOWING PINS AS APPROPRIATE. USE CRIMPING TOOL AMP CAT.

#90277-1.

16-18 AWG AMP CAT. #66101-3

20-22 AWG AMP CAT. #66399-3

24-26 AWG AMP CAT. #66109-3

AMP8P			EIGHT PIN CONNECTOR, MALE CIRCULAR PLUG, SHELL 						4PR22OS

SIZE 11-8, AMP CAT. #206434-1 BACK SHELL AMP

CAT. #206062-3. USE THE FOLLOWING PINS AS

APPROPRIATE. USE CRIMPING TOOL AMP CAT #90277-1.

16-18 AWG AMP CAT. #66099-3

20-22 AWG AMP CAT. #66400-3

24-26 AWG AMP CAT. #66107-3

AMP8S			EIGHT PIN CONNECTOR, FEMALE CIRCULAR PLUG, SHELL					4PR22OS

SIZE 11-8, AMP CAT. #205838-1 BACK SHELL AMP

CAT. #206062-3. USE THE	FOLLOWING PINS AS

APPROPRIATE. USE CRIMPING TOOL AMP CAT. #90277-1.

16-18 AWG AMP CAT. #66101-3

20-22 AWG AMP CAT. #66399-3

24-26 AWG AMP CAT. #66109-3

AMP9F			NINE PIN CONNECTOR, SERIES 1 LIGHTWEIGHT FEMALE						4PR24FRP

CIRCULAR PLASTIC CONNECTOR(CPC). AMP CAT#206708-1

AMP9S			NINE PIN CONNECTOR, FEMALE CIRCULAR PLUG, SHELL 		MAGNET MOVERS	9C18J

SIZE 11-9, AMP CAT. #206485-1, BACK SHELL AMP

CAT. #206062-3. USE THE FOLLOWING PINS AS

APPROPRIATE. USE CRIMPING TOOL AMP CAT. #90277-1.

16-18 AWG AMP CAT. #66101-3

20-22 AWG AMP CAT. #66399-3

24-26 AWG AMP CAT. #66109-3

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

AMP9SA		NINE PIN CONNECTOR, FEMALE CIRCULAR PLUG, SHELL

SIZE 13-9, AMP CAT. #206708-1, BACK SHELL AMP

CAT. #206966-1. USE THE FOLLOWING PINS AS APPROPRIATE.

USE CRIMPING TOOL	AMP CAT. #90277-1.

16-18 AWG AMP CAT. #66101-3

20-22 AWG AMP CAT. #66399-3

24-26 AWG AMP CAT. #66109-3

AMP12P		CONNECTOR, 12 PIN MALE, AMP CAT-# 204740-2 SLAC

S/N59-299-162-52.

CABLE CLAMP AMP CAT #205083-1.USE CRIMPING TOOL

AMP#584-95-1.USE THE FOLLOWING PINS AS APPROPRIATE:

#20-24 AWG, #203816-4 (LOOSE), S/N59-299-805-51.

#20-24 AWG, #203816-2 (REELED).

#26-30 AWG, #203874-4 (LOOSE), S/N59-299-805-52.

#26-30 AWG, #203874-2 (REELED).

AMP14P		FOURTEEN PIN CONNECTOR, MALE, PLASTIC SHELL, AMP

CAT #206044-1 WITH CABLE CLAMP KIT AMP CAT. #206070-1.

USE CRIMPING TOOL AMP #584-95-1.

USE THE FOLLOWING PINS,AS APPROPRIATE

#32-30 AWG AMP CAT #201555-1

#28-24 AWG AMP CAT #201334-1

#24-20 AWG AMP CAT #201330-1

#18-16 AWG AMP CAT #202507-1

#14    AWG AMP CAT #201570-1

AMP14SR		FOURTEEN PIN CONNECTOR, FEMALE, PLASTIC SHELL,

AMP CAT #206043-1, CABLE CLAMP KIT AMP CAT #206070-1.

USE THE FOLLOWING PINS, AS APPROPRIATE. USE CRIMPING

TOOL AMP. #584-95-1.

#32-30 AWG AMP CAT #201554-1

#28-24 AWG AMP CAT #201332-1

#24-20 AWG AMP CAT #201328-1

#18-16 AWG AMP CAT #202508-1

#14    AWG AMP CAT #201568-1

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

AMP24P		TWENTY-FOUR POSITION RECEPTACLE, MALE, AMP			MPS TOROIDS		6PR24IS

CAT-# 204742-2 SLAC P/N59-299-162-54, WITH CABLE CLAMP

#205083-2, S/N59-299-162-94. USE THE FOLLOWING PINS, AS

APPROPRIATE: USE CRIMPING TOOL AMP #584-95-1.

#20-24 AWG, #203816-4 (LOOSE), S/N59-299-805-51.

#20-24 AWG, #203816-2 (REELED), S/N59-299-805-53.

#26-30 AWG, #203874-4 (LOOSE), S/N59-299-805-52.

#26-30 AWG, #203874-2 (REELED), S/N59-299-805-54.

WHEN USED WITH 6PR24IS CABLE FOR MPS TOROIDS, WIRE AS FOLLOWS:

PAIR#   WIRE#     PIN#    PAIR#   WIRE#     PIN#

1       A         A1      4       A         A4

1       B         B1      4       B         B4

1       SHIELD    C1      4       SHIELD    C4

2       A         A2      5       A         A5

2       B         B2      5       B         B5

2       SHIELD    C2      5       SHIELD    C5

3       A         A3      6       A         A6

3       B         B3      6       B         B6

3       SHIELD    C3      6       SHIELD    C6

AMP36P		THIRTY-SIX POSITION PLUG ASSEMBLY, AMP 204744-2, SLAC					18PR22OS, RG58

STANDARD CAMAC CABLE PLUG, SLAC S/N59-299-162-55, WITH

CABLE CLAMP #205083-3, S/N59-299-162-95.

USE CRIMPING TOOL AMP #584-95-1. USE THE FOLLOWING PINS,

AS APPROPRIATE:

#20-24 AWG, #203816-4 (LOOSE), S/N59-299-805-51.

#20-24 AWG, #203816-2 (REELED), S/N 59-299-805-53.

#26-30 AWG, #203874-4 (LOOSE), S/N59-299-805-52.

#26-30 AWG, #203874-2 (REELED), S/N59-299-805-54.

AMP37P		THIRTY-SEVEN PIN CONNECTOR, MALE, CPC, AMP CAT.

#206305-1 BACK SHELL CABLE CLAMP AMP CAT. #206138-1,

#16 AWG, PINS AMP CAT. # 40-102C. USE HAND CRIMPING

TOOL AMP CAT. #90067.

AMP37S		THIRTY-SEVEN PIN CONNECTOR, FEMALE, CPC, AMP CAT.

#206150-1 BACK SHELL CABLE CLAMP AMP CAT. #206138-1,

#16 AWG, PINS AMP CAT. # 40-103C. USE HAND CRIMPING

TOOL AMP CAT. #90067.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

AMP48P		FORTY-EIGHT POSITION PLUG ASSEMBLY, AMP 204733-2,					18PR22OS, 30PR26OS

SLAC STANDARD CAMAC CABLE PLUG, SLAC S/N59-299-162-06,

WITH CABLE CLAMP #205083-4, S/N59-299-162-96.

USE CRIMPING TOOL AMP #584-95-1. USE THE FOLLOWING PINS,

AS APPROPRIATE:

#20-24 AWG, #203816-4 (LOOSE), S/N59-299-805-51.

#20-24 AWG, #203816-2 (REELED),S/N59-299-805-53.

#26-30 AWG, #203874-4 (LOOSE),S/N59-299-805-52.

#26-30 AWG, #203874-2 (REELED),S/N59-299-805-54.

AMP50P		FIFTY POSITION MALE PLUG ASSEMBLY, SOLDER				DISABLE/ALARM	25PR24OS

CONNECTIONS, AMP P/N 229912-1

AMP50S		FIFTY POSITION FEMALE PLUG ASSEMBLY, SOLDER			DISABLE/ALARM	25PR24OS

CONNECTIONS, AMP P/N 229913-1

AMPH2			TWO PIN CONNECTOR, 1 MALE, 1 FEMALE. BNC POLARIZED

CONTACTS. AMPHENOL NO. 31-224.

AMPH4			FOUR PIN CONNECTOR, AMPHENOL NO. 206136-1.USE CRIMPING

TOOL, AMP NO. 69710-1. WIRE IN COLOR CODE SEQUENCE.

SEE THE WIRE TYPE FOR THE COLOR CODE.

AMPH7S		SEVEN PIN CONNECTOR, FEMALE, ISI/MDC P/N 992-1002.

SEE THE WIRE TYPE FOR THE COLOR CODE. SOLDER

CONNECTIONS.

AMPH8S		EIGHT PIN CONNECTOR, OCTAL TUBE SOCKET AMPHENOL

NO. 78-S8, USE AMPHENOL CAP NO. 86-3-24. SEE THE

WIRE TYPE FOR THE COLOR CODE. SOLDER CONNECTIONS.

AMPL2			CABLE PLUG, TWO CONDUCTOR IN LINE, MATE-N-LOCK

CONNECTOR, AMP P/N 1-480698-0.

USED FOR REPEATER CHASSIS J2.

BBJ58			COAXIAL CONNECTOR, BNC BULKHEAD JACK.							RG58

TYCO PART # 1-1337434-0. SEE TYCO DRAWING # C-1337434

( http://www.farnell.com/datasheets/23770.pdf )

FOR STRIPPING DIMENSIONS.

USE TYCO HAND TOOL 9-1478240-0.

USE TYCO DIE SET 9-1478242-0.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

BBJ59			COAXIAL CONNECTOR, BNC BULKHEAD JACK, KINGS 			SLCNET		RG59DS

P/N'S 19-62, KC19-182 OR KC19-89,

SLAC S/N59-299-014-66. TRIM CODE 405,

USE KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2002.

BBJ214		COAXIAL CONNECTOR, N BULKHEAD JACK, KINGS P/N KC-19-232,	PANEL MOUNTS	RG214

SLAC S/N59-299-014-71. USE TRIM CODE 411, USE KINGS

CRIMPING TOOL KTH-1000 WITH DIE KTH-2004

BNC58			COAXIAL CONNECTOR, BNC CABLE PLUG, UG-88D/U. KINGS CAT.	RF AND FAST		RG58

NO. KC-59-290 OR KC-59-291, SLAC S/N59-299-014-51. USE	SIGNALS

KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2001 AND TRIM

CODE 401.

BNC59			COAXIAL CONNECTOR, BNC CABLE PLUG, UG-260B/U. KINGS CAT.	TV			RG59, RG59DS

NO. KC-59-293 OR KC-59-294, SLAC S/N59-299-014-52. USE

KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2002 AND TRIM

CODE 401.

BNC62			SAME CONNECTOR AS BNC59. SAME TOOLING AND TRIM CODE.		SSC FASTLINK	RG62

BNC174		COAXIAL CONNECTOR, BNC CABLE PLUG, KINGS #KC-59-557-M06

SLAC S/N59-299-014-63, TRIM CODE 406. USE CRIMPING TOOL

KTH-1000 WITH SIE KTH-2032.

BNC213		COAXIAL CONNECTOR, BNC CABLE PLUG. KINGS CAT. NO.		RF AND FAST		RG213, RG8

KC-59-86, USE KINGS CRIMPING TOOL KTH-1000 WITH DIE		SIGNALS

KTH-2003 AND TRIM CODE 209A.

BNC214		COAXIAL CONNECTOR, BNC CABLE PLUG. KINGS CAT. NO.		RF AND FAST		RG214

KC-59-85, USE KINGS CRIMPING TOOL KTH-1000 WITH DIE		SIGNALS

KTH-2004 AND TRIM CODE 209A

BNC223		COAXIAL CONNECTOR, BNC CABLE PLUG. KINGS CAT. NO.		RF AND FAST		RG223

KC-59-80 OR KC-59-162, SLAC S/N. 59-299-014-65.			SIGNALS

USE KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2001

AND TRIM CODE 401.

BNC240		IT IS BASICALLY A BNC MALE CONNECTOR WHICH ATTACHES TO AN				LMR240, LMR240FR

LMR240FR CABLE.THE DESCRIPTION IS COAXIAL CONNECTOR TYPE

BNC MALE PLUG. TIMES MICROWAVE,SYSTEMS CATALOG

#TIMTC240BM-A CONNECTOR, BNC MALE CRIMP FOR LMR240,

LMR240FR.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

BNCKAP		COAXIAL CONNECTOR, BNC CABLE PLUG FURNISHED WITH					KAPTON

KAPTON CABLE TYPE ONLY.

BNC-TWN		   TWIN BNC CONNECTOR PLUG, MANUFACTURED BY TYCO 		 SOLID STATE	     TWC-78FR

ELECTRONICS,(OLD P/N: CAT. 1307191). Use P/N: 5332225.	 SUB-BOOSTER

TRIGGERS

BP(-ccc)		BANANA PLUG, WITH COLORED PLASTIC INSULATING SHELL.

WHERE (-ccc) IS DEFINED, THE SHELL IS TO BE THE

INDICATED COLOR. IF UNDEFINED, ANY COLOR MAY USED.

SLAC S/N 59-299-698-(nn), WHERE (nn) IS SELECTED

FOR THE DESIRED COLOR.

BP&BJ			BANANA PLUG (MALE) AND BANANA JACK (FEMALE) SLAC					3C16/3V

P/N 59-299-698-(nn)& SLAC P/N 59-299-699-(nn). WHERE

(nn)IS SELECTED FOR THE DESIRED COLOR.

BP-01			TERMINATION BP ABOVE, WITH (ccc) SELECTED TO MATCH THE

WIRE COLOR(S) OF THE INDICATED CABLE.

BP-02			TERMINATION BP ABOVE, USING THE FOLLOWING COLORS, AND					2C16OS, 1PR20OS

CONNECTED TO THE MATCHING COLORED JACKS ON THE

INDICATED CHASSIS.

BLACK WIRE WITH A BLUE BANANA PLUG (SLAC S/N 59-299-698-07).

WHITE WIRE WITH A BLACK BANANA PLUG (SLAC S/N 59-299-698-05).

SHIELD WIRE WITH A GREEN BANANA PLUG (SLAC S/N 59-299-698-06).

BPD-01		BANANA PLUG DUAL, BLACK COLORED PLASTIC INSULATING SHELL.

SLAC S/N 59-299-701-01. MFG: POMONA. MFG P/N: 1330-0

BSB			CONNECTOR, BUTT SPLICE, BLUE, INSULATED,

FOR #14 TO #16AWG.WIRE, AMP CAT.#320562,

SLAC S/N59-294-770-07. USE HAND CRIMPING TOOL

AMP #59250.

BSR			CONNECTOR, BUTT SPLICE, RED, INSULATED,							3PR24OS

FOR #18 TO #22 AWG. WIRE,AMP CAT.#320559,

SLAC S/N59-294-770-04. USE HAND

CRIMPING TOOL AMP #59250.

BSY			CONNECTOR, BUTT SPLICE, YELLOW, INSULATED,

FOR #10 TO #12 AWG.WIRE, AMP CAT.#320570,

SLAC S/N59-294-770-09. USE HAND

CRIMPING TOOL AMP #59239-4R.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

BS1			CONNECTOR, BUTT SPLICE FOR #1 AWG WIRE,

UNINSULATED, COPPER, LONG BARREL,

BURNDY CAT. #YS1C. USE CRIMPING TOOL

BURNDY #MY29-11 WITH DIE BURNDY #U/CRT.

BS2               CONNECTOR, BUTT SPLICE FOR #2 AWG WIRE, UNINSULATED,

COPPER, LONG BARREL. MFG: THOMAS AND BETTS. P/N:54507.

BS2/0			CONNECTOR, BUTT SPLICE FOR 2/0 AWG WIRE,

UNINSULATED,COPPER, LONG BARREL,COLOR-KEYED

CAT.#54810. USE CRIMPING TOOL

"COLOR-KEYED TBM8" WITH DIE "COLOR-KEYED #13462".

BS35ALC     	CONNECTOR, BUTT SPLICE, 350 KCMIL, ALUMINUM TO COPPER, UNINSULATED,

CAN BE USED TO SPLICE AL/CU FOR WIRE RANGE OF 2/0-350 KCMIL

WHEN USED WITH “VERSA-CRIMP” CRIMPER.

MFG: HUBBELL-ANDERSON, MFG P/N: VACS-350.

LINK: http://www.hubbell.com.mx/pdfs/anders.pdf PAGE: A-55

BS4			CONNECTOR, BUTT SPLICE FOR #4 AWG WIRE,

UNINSULATED, COPPER, LONG BARREL, BURNDY

CAT. #YS4C. USE CRIMPING TOOL

BURNDY #MY29-11 WITH DIE BURNDY #U4CRT.

BS4/0			CONNECTOR, BUTT SPLICE FOR 4/0 AWG WIRE,

UNINSULATED,COPPER, LONG BARREL, COLOR-KEYED

CAT.#54812. USE CRIMPING TOOL

"COLOR-KEYED TBM8" WITH DIE

"COLOR-KEYED #13463".

BS8		   CONNECTOR, BUTT SPLICE FOR #8 AWG WIRE, UNINSULATED,

COPPER, LONG BARREL. MFG: THOMAS AND BETTS. P/N: 54504.

BULLET		BULLET WIRE TERMINATION, SLAC S/N59-294-644-01,			SUMP PUMP ALARM	4C18OS

BURNDY CAT. #AYH-18-H2. USE HAND CRIMPING TOOL

BURNDY #M8ND WITH DIE BURNDY #N18HCT.

BUR20S		CONNECTOR, 20 PIN FEMALE, RECTANGULAR PLUG,

BURNDY P/N MS20PM-824S. INCLUDES HOOD,

SKIRT AND JACK SCREWS.

C41SW			COAXIAL CONNECTOR,MALE,PLATED,TYPE N,

ANDREWS PN F1PNM-14.

C41SWS		COAXIAL CONNECTOR, SMA MALE, ANDREWS PN F1PSM.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

CAN4P			FOUR PIN CONNECTOR, MALE, SOLDER TERMINATIONS,

CANNON CAT #WK-4-22C.

CAN4S			FOUR PIN CONNECTOR, FEMALE, SOLDER TERMINATIONS,

CANNON CAT #WK-4-21C.

CAN12S		TWELVE PIN CONNECTOR, FEMALE, SOLDER							RG214

TERMINATIONS, CANNON CAT #GK1221

CAN24S		TWENTY-FOUR PIN CONNECTOR, FEMALE, BAYONET						12C12/3V

SERIES, SOLDER PINS, USE HEAT SHRINK TUBING OVER EVERY

OTHER SOLDER POCKET FOR INSULATION. CANNON-ITT CAT.

#CA3106F24A-24S.

CATON13		THIRTEEN PIN CIRCULAR PLUG WITH CABLE CLAMP,

CATON PART #3106A-CC18-135.

CED-30		CARD EDGE CONNECTOR, DOUBLE ROW, 30-POINT FEMALE.

CINCH-JONES P/N 250-50-38A-30.

CIN12S		TWELVE PIN FEMALE CONNECTOR, CINCH P/N 9142,

USE HOOD P/N 60332.

CIN20S		TWENTY PIN FEMALE CONNECTOR, CINCH P/N 9325,

USE HOOD P/N 60326.

CUT			CONNECTOR TYPE UNKNOWN AT THIS TIME, TERMINATION IS BE

DONE BY OTHER LATER, PULL CABLE TO ORIGIN/DESTINATION

IN LEAVE TWO FEET AT THE EXIT.

D14S			FOURTEEN PIN FEMALE "D" CONNECTOR AMPHENOL P/N

57-60140 ASSEMBLE WITH CABLE HOUSING (BACK SHELL) AND

SPRING LATCH PLATE 17-529

DAC15P		CONNECTOR, 15 PIN MALE, CANNON "D" SERIES							3PR24IS

SUBMINIATURE, CANNON CAT.#DAU-15P SLAC

P/N59-299-160-01.

DAY-20		TWENTY POSITION CARD EDGE SPECIAL CONNECTOR,			LVDT			3PR24IS, 2PR24IS

DAYTRONICS PN #60322 WITH DUAL CABLE CLAMPS AND SOLDER				4C20OS

TYPE PINS. REFERENCE DRAWING BD-129-691-03

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

DAY-50		FIFTY POSITION CARD EDGE CONNECTOR ADAPTED BY PC BOARD				12PR22OS

TO A 17 SCREW CONNECTING STRIP. TOP TO BOTTOM:

1-EXT.COLLECTOR POWER, 2-ISOLATED COMMON,3/17-CH's 0-15.

DAYTRONICS PN #XXXXXXX

DB9MFV		PRE-FABRICATED COMPUTER CABLE D-SUB 9 PIN MALE TO FEMALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPLLIERS, IE. "FRY'S ELECTRONICS"

DB9MMV		PRE-FABRICATED COMPUTER CABLE D-SUB 9 PIN MALE TO MALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPLLIERS, IE. "FRY'S ELECTRONICS"

DB9P			NINE PIN CONNECTOR, MALE, "D" SUBMINIATURE						2PR22OS

RECTANGULAR, ITT CANNON CAT. #DEU-9P,

SLAC S/N59-299-160-05,HOOD ITT CANNON

CAT. #DE24657 SLAC S/N59-299-160-50.

LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1

DB9S			NINE PIN CONNECTOR, FEMALE, "D" SUBMINIATURE						5PR28F, 6PR22OS

RECTANGULAR, ITT CANNON CAT. #DEU-9S.

SLAC S/N59-299-160-06, HOOD ITT CANNON

CAT. #DE24657, SLAC S/N59-299-160-50.

LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

DB15P			FIFTEEN PIN CONNECTOR, MALE, "D" SUBMINIATURE

RECTANGULAR, ITT-CANNON CAT. #DAU15P, SLAC

S/N59-299-160-01, HOOD ITT CANNON CAT. #DA24658,

SLAC S/N59-299-160-51.LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

DB15S			FIFTEEN PIN CONNECTOR, FEMALE,"D" SUBMINIATURE						8PR28F

RECTANGULAR,ITT-CANNON CAT. #DAU15S, SLAC

S/N 59-299-160-02, HOOD ITT-CANNON CAT.#DA24658.

SLAC S/N59-299-160-51.LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

DB15S-HD	   DB15 HIGH DENSITY SOCKET - THE 15-PIN CONNECTOR

WILL HAVE 3 ROWS OF 5 SOCKETS.CONNECTOR IS TYPICALLY FOUND

FOR VIDEO CABLE TO COMPUTER MONITORS.

MFG:STARTECH COMPUTER PRODUCTS, MFG P/N:C15HPSF

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

DB25MFV		PRE-FABRICATED COMPUTER CABLE D-SUB 25 PIN MALE TO FEMALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPLLIERS, IE. "FRY'S ELECTRONICS"

DB25MMV		PRE-FABRICATED COMPUTER CABLE D-SUB 25 PIN MALE TO MALE

WITH MOLDED PLUG ENDS. WIDELY AVAILABLE FROM COMPUTER

RETAILERS AND PART SUPPLIERS, IE. "FRY'S ELECTRONICS"

DB25P			TWENTY-FIVE PIN CONNECTOR, MALE, "D"							26C24OS

SUBMINIATURE RECTANGLE, ITT-CANNON CAT. #DBC-25P, SLAC

S/N59-299-160-03, HOOD ITT-CANNON CAT. DB24659, SLAC

S/N59-299-160-52. LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

DB25S			TWENTY-FIVE PIN CONNECTOR, FEMALE, "D"							26C24OS

SUBMINIATURE RECTANGLE, ITT-CANNON CAT. #DBU-25S, SLAC

S/N59-299-160-04, HOOD ITT-CANNON CAT. #DB24659, SLAC

S/N59-299-160-52. LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1. FOR 18-22AWG WIRE, USE THE

FOLLOWING DIGIKEY SOCKETS: A31900TR-ND

DB37P			THIRTY SEVEN PIN CONNECTOR MALE "D" SUBMINIATURE RECTANGLE.

DB37S			THIRTY SEVEN PIN CONNECTOR FEMALE "D" SUBMINIATURE RECTANGLE.

DB50			50 PIN AMPLITE HDP-20 (DB50) SHIELDING HARDWARE ENCLOSER KIT

AMP PART NUMBER 747959-1 (1 REQUIRED)

HDP-20 SERIES STEPPED FERRULE (0.375 TO 0.432 DIA CABLE OD)

AMP PART NUMBER 747580-4 (1 REQUIRED)

PIN CONTACT - 24 TO 28 AWG - 30 MICRON GOLD FINISH

AMP PART NUMBER 66505-9 (50 REQUIRED)

DB52P			FIFTY-TWO PIN CONNECTOR, MALE, "D" SUBMINIATURE						18PR22OS

RECTANGULAR, ITT-CANNON,CAT. #2DB52P, SLAC S/N59-299-160-07.

HOOD ITT-CANNON CAT. #DD24661. LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

DB52S			FIFTY-TWO PIN CONNECTOR, FEMALE, "D"							18PR22OS

SUBMINIATURE RECTANGULAR, ITT-CANNON CAT. #2DB52S,

SLAC S/N59-299-160-08, HOOD ITT-CANNON CAT. #DD24661.

LOCK DEVICES S/N59-299-160-74.

USE CRIMPING TOOL AMP #584-95-1.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

DD50S			FIFTY PIN CONNECTOR, FEMALE, SOLDER TERMINATIONS,

COMMERCIAL "D" SUBMINIATURE. THIS CONNECTOR

CONSISTS OF THE FOLLOWING PARTS:

CONNECTOR - ITT CANNON P/N DD50S

SHELL - ITT CANNON P/N DD24661

SCREW LOCK - ITT CANNON P/N D20420

DIN3			THREE PIN CONNECTOR, SPECIAL APPLICATION FOR PRESSURE

TRANSDUCER AND SOLENOID VALVE, DIN 43650/ISO 4400.

OMEGA P/N CX5302.

DIN6P			SIX PIN CONNECTOR, MALE, DIN PLUG. SPECIAL APPLICATION FOR

LAKESHORE TEMPERATURE CONTROLLER MODEL 340.

SUPPLIER: LAKESHORE, 575 MCCORKLE BLVD, WESTERVILLE, OH 43082,

(614)891-2244. P/N: 106-233

DIN96P		NINETY-SIX PIN CONNECTOR, MALE, 3X32 DIN CONNECTOR,		VSAM

HARTING ELECTRONICS BRAND. P/N#09-03-096-3214

SHELL HOUSING: 09-03-96-0501.

CABLE INSERTS:   09-02-000-9911.

LOCKING LEVERS: 09-02-000-9902 (L), 09-02-000-9903 (R)

DISHI			This is a Burndy Minilock pin that is no longer available.

It is not recommended to make any terminations to the area

called "DISHI" as it is very unreliable.

D37FLT		THIRTY SEVEN PIN CONNECTOR, D-SUBMINIATURE FOR FLAT

CABLE. AMPHENOL CAT. #841-17DCFR-B37P.

D37P			THIRTY SEVEN PIN CONNECTOR, MALE, "D" AMP

#17-20370-1 ASSEMBLE WITH CABLE HOUSING (BACK SHELL)

17-313-01, AND SPRING LATCH PLATE 17-259. USE CRIMP PIN

17-766-02, AND INSTALL USING CRIMP TOOL 357-100 WITH PIN

LOCATOR BUSHING 357-300-2.

D37S			THIRTY SEVEN PIN CONNECTOR, FEMALE, "D" AMP			SLC SLITS		12C16/3V

#17-10370-1 ASSEMBLE WITH CABLE HOUSING (BACK SHELL)

17-313-01, AND SPRING LATCH PLATE 17-529. USE CRIMP PIN

17-763-02, AND INSTALL USING CRIMP TOOL 357-100 WITH PIN

LOCATOR BUSHING 357-300-2.

D50FLT		FIFTY PIN CONNECTOR, D-SUBMINIATURE FOR FLAT CABLE.

SLAC S/N59-299-165-50.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

D50F			A THREE PART CONNECTOR CONSISTING OF: CONNECTOR 					12C16/3V

RECEPTACLE, JUNCTION SHELL AND SCREW LOCK ASSEMBLY.

THESE ARE LBL STOCK ITEMS. THE RESPECTIVE PART NAMES

AND STOCK NUMBERS ARE:

CONNECTOR - AMPHENOL PN #17-10500-1 LBL #5935-34166

SHELL - ITT CANNON PN #DD24661 LBL #5935-57869

SCREW LOCK - ITT CANNON PN #D20419-12 LBL #5935-67234

F59B			COAXIAL CONNECTOR, TYPE F CABLE PLUG, NEWARK P/N 32N1129,				RG59

TYPE CP5F9-1/8. NOTE THAT THE COAX SOLID CENTER

CONDUCTOR IS THE MALE PIN. USE KINGS CRIMPING TOOL KTH-

1000 WITH DIE KTH-2002 AND TRIM CODE 401.

F59QS			COAXIAL CONNECTOR, TYPE "F" CABLE PLUG, SIGNAL			SLCNET AND		RG59QS

VISION.CAT. #QF59-RNS-QD. NOTE THAT THE COAXIAL SOLID		FFNET TAPS

CENTER. CONDUCTOR IS THE MALE PIN. USE THE FOLLOWING

TOOLS TO ASSEMBLE CONNECTOR:

1. STRIPPING TOOL SIGNAL VISION CAT. #QF-ST

2. QF COMPRESSION TOOL SIGNAL VISION CAT. #QF-CT

3. INSERTION TOOL RILEY CO. CAT. #ITF-59,6,11

FIOP-ST		FIBER OPTIC CONNECTOR. TYPE 'ST' LIGHTGUIDE						FIOPMM12, 24, 48, 52

CONNECTOR, CERAMIC TIP, BAYONET-TYPE TWIST LOCK MFG

AT&T. P/N P2020C-C-125, COMCODE 105 143 911.

FIXED			THE CABLE IS FIXED TO, AND AN INTEGRAL PART OF A UNIT OR	SLC FF TRIPLET	RG59

DEVICE. THE CABLE IS NOT INTENDED TO BE FIELD REPAIRED	TEMP.MON.SYS.

OR REPLACED.

FLAG-1		TERMINAL, SLAC MANUFACTURED, 6061 ALUMINUM, 1 HOLE					1”WCAL

CABLE FLAG WATER COOLED.

FLAG-2		TERMINAL, SLAC MANUFACTURED, 6061 ALUMINUM, 2 HOLE

CABLE FLAG WATER COOLED. 1"WCAL

F1/2RP		COAXIAL CONNECTOR, "F" FEMALE, FOR SEMI-RIGID						1/2" RD, 3PR24IS

JT-4500 SERIES COAXIAL CABLE. GILBERT PART NO.

GRS-500-BAFF-DU-03. SEE THE GILBERT CATALOG

FOR TRIM AND ASSEMBLY INSTRUCTIONS.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

FO-SPL		FIBER OPTIC ROTARY MECHANICAL SPLICE. THIS SPLICING					FIOPMM12, FIOPMM24,

REQUIRES A 1040AB TOOL KIT, A D181617 CONSUMABLES KIT,				FIOPMM48, FIOPMM52

AT-8995 INDEX MATCHING GEL AND REAGENT GRADE ALCOHOL.

THE SPLICE IS STORED IN A UC-SS/M1 ORGANIZER AND IN A

MECHANICAL TRAY. TERMINATION IS TO BE PERFORMED BY

TRAINED AND AUTHORIZED PERSONNEL ONLY.

FUSION		FUSION SPLICING OF FIBER OPTIC CABLE ENDS. SPLICES WILL

BE CONTAINED IN A HEAT SHRINK SLEEVE WITH A SMALL METAL

ROD FOR STRENGTH. SPLICES MAY BE FURTHER PLACED IN TRAY

FOR ADDITIONAL PROTECTION AND FIBER MANAGEMENT.

GH-4M			FOUR PIN CONNECTOR, MALE. THIS CONNECTOR IS SUPPLIED 		VACG

WITH THE COLD CATHODE MODULE FROM MKS INSTRUMENTS INC.

GP-20S		TWENTY PIN CONNECTOR, FEMALE. THIS CONNECTOR IS SUPPLIED

BY GRANVILLE-PHILLIPS WHEN A MODEL 350 ION GAUGE

CONTROLLER IS ORDERED.

GP-CON		USE CED-30 CONNECTOR. WIRE AS SHOWN BELOW, USING					9C18J

THE INDICATED CABLE COLOR-CODE FOR SEQUENCE. NINE PINS

ARE CONNECTED AS INDICATED. OTHER PINS AND/OR WIRES ARE

NOT CONNECTED.

CED-30

PIN # PAIR # WIRE #

01

05

07

08

09

10

11

13

14

GP-GAU		SPECIAL PREWIRED 6-PIN (IG-CP6) AND BNC CONNECTORS					IG-CABLE

FOR CONNECTION OF AN ION-GAUGE TO A GRANVILLE-PHILLIPS

SERIES 270 ION-GAUGE CONTROLLER.

HALPRB1		CONNECTOR, 40 PIN, MPT-132-30S (01391083),

GROUP 3 TECH., AUCKLAND, NEW ZEALAND.

HALPRB2		CONNECTOR, 40 PIN, MPT-132-30S (01391084),

GROUP 3 TECH., AUCKLAND, NEW ZEALAND.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

HALPRB3		CONNECTOR, 40 PIN, MPT-132-15M (01391054),

GROUP 3 TECH., AUCKLAND, NEW ZEALAND.

HN213			COAXIAL CONNECTOR, TYPE HN CABLE PLUG, KINGS CAT.					RG213R

#KH-59-19, 50 OHM, SLAC P/N59-299-020-54.,5KV,

HV RATING. USE CRIMPING TOOL KTH-1000 WITH

DIE KTH-2003 AND TRIM CODE 402.

HN214			COAXIAL CONNECTOR, TYPE HN CABLE PLUG, KINGS CAT-#					RG214

KH-59-21, SLAC P/N59-299-020-55, 5KV, HV RATING.

USE KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH 2004

AND TRIM CODE 402M.

HN214M		COAXIAL CONNECTOR, TYPE HN CABLE PLUG. KINGS CAT. NO.		INJ. KICKER

KN-59-21, MODIFIED TO SPECIFICATIONS AS SHOWN ON DRAWING	MODULATOR

# CA-344-296-00. CONNECTOR TERMINATES A TMS8481 COAXIAL

CABLE. USE KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2004

SEE DRAWING # CA-344-296-00 FOR CABLE TRIM CODE.

HPJ			SIX PIN CONNECTOR, FEMALE, HP SPECIAL. PRE-WIRED ONTO		RF POWER METER	HP-CORD

ONE END OFAN HP POWER METER CABLE.

HPP			SIX PIN CONNECTOR, MALE, HP SPECIAL. PRE-WIRED ONTO 		RF POWER METER	HP-CORD

ONE END OF AN HP POWER METER CABLE.

HR13P			THIRTEEN PIN MALE RECEPTACLE, HIGH RADIATION,			ARC PPS

CERAMIC INSULATED, BEAM SWITCHYARD REMOTE OPERABLE		(STOPPERS)

DISCONNECT, SLAC BUILT. REFERENCE SLAC 887-006

DRAWING PACKAGE AND WD-233-702-00.

HR13S			THIRTEEN PIN FEMALE RECEPTACLE, HIGH RADIATION,			ARC PPS		4PR16TC

CERAMIC INSULATED, BEAM SWITCHYARD REMOTE OPERABLE		(STOPPERS)

DISCONNECT, SLAC BUILT. REFERENCE SLAC 887-006

DRAWING PACKAGE AND WD-233-702-00.

HRS4			FOUR PIN CONNECTOR, FEMALE, PLASTIC, SUB-MINIATURE,

MFR HRS (JAPAN) P/N DF13-45-1.25C.

HV-C			COAXIAL CONNECTOR, 10KV HV CABLE PLUG. REYNOLDS CAT.		ION CHAMBERS	TYPE-C

NO. 167-3554. 								SSRL ION PUMPS

HV-CBJ		COAXIAL CONNECTOR, 10KV BULKHEAD JACK,

KINGS CAT.#1062-2.USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE KTH-2001 AND TRIM CODE 484.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

HVW213		COAXIAL CONNECTOR, 10KV CABLE PLUG. W.W. FISCHER		VACP SYS		RG213R

CAT. #S105A108/10.7

HVWTIME		COAXIAL CONNECTOR, 10KV CABLE PLUG. W.W. FISCHER		VACP SYS		TIMES, TYPE-C

CAT.#S105A108/5.2.										RG58R

HV58			COAXIAL CONNECTOR, 10KV HV CABLE PLUG,							RG58R, TYPE-C

KINGS CAT. #1065-2, SLAC S/N59-299-034-01.

USE CRIMPING TOOL KTH-1000 WITH DIE

KTH2001 AND TRIM CODE 419.

HV58J			COAXIAL CONNECTOR, 10KV HV CABLE JACK,							TYPE-C

KINGS CAT. #1062-2, USE KINGS CRIMPING

TOOL KTH-1000 WITH DIE KTH-2001 AND

TRIM CODE 419 AND HEAT GUN.

HV213			COAXIAL CONNECTOR, 20KV HV CABLE PLUG. KINGS CAT.		ION PUMP POWER	RG213R

NO. 1765-1 OR REYNOLDS CAT. NO. 167-3516, S/N.			SUPPLY END

59-299-033-01. USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE KTH-1078 OR -2078 AND TRIM

CODE 475 OR DIE KTH-2003 AND TRIM

CODE REY2, RESPECTIVELY.

HV214			USE HV213 CONNECTOR, WITH A LARGER FERRULE (SLEEVE)		PLIC			RG214

FOR RG214, KINGS P/N #S89-24-2, SLAC S/N59-299-009-06.	SYSTEM

INSTALL A 6" PIECE OF RED SHRINK TUBING AT EACH

END OF CABLE 3" FROM THE CONNECTOR. USE CRIMPING

TOOL KTH-1000 WITH DIE KTH-1079 AND TRIM CODE 475.

HV220			SPECIAL SLAC HV CONNECTOR AND CONNECTIONS. SEE CABLE		KLYSTRON HV		RG220, HVSPEC1

INSTALLATION GROUP OR SLAC ELECTRONICS GROUP FOR

DETAILS. HV CONNECTOR, ISOLATION DESIGN INC. MODEL

D-103-SL.

IG20			TWENTY PIN CONNECTOR, FEMALE, POSITRONIC IND. P/N

GM20FSCDOJUL-734.0. THIS CONNECTOR IS SUPPLIED BY

THE MFR. WHEN ORDERING A GRANVILLE-PHILLIPS

IONIZATION GAUGE CONTROLLER MODEL 330

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

IG21			FOUR PIN CONNECTOR, FEMALE PINS, CANNON CAT. NO.		ION-GAU

SK-U4-21C-1/2. ION GAUGE WIRE AS FOLLOWS:				ARC BOX

BLK #14 AWG UNSHIELDED WIRE TO PIN #1

RED #14 AWG UNSHIELDED WIRE TO PIN #2

BLK #16 AWG SHIELDED WIRE TO PIN #3

CLEAR #16 AWG SHIELDED WIRE TO PIN #4(COAX CENTER PIN)

THE TWO SHIELDS ARE TO BE CONNECTED TOGETHER AND TO THE

PIN #4 COAXIAL SLEEVE. THE SHIELDS MUST NOT TOUCH THE

CONNECTOR SHELL.THE COAXIAL PIN IS PART OF A SPECIAL

ELECTROMETER CIRCUIT, AND MUST BE KEPT

EXTREMELY CLEAN REFER TO DWG. CA-208-102-01-R0

IG22			FOUR PIN CONNECTOR, MALE PINS, CANNON CAT. NO.			ION GAUGE		ION-GAU

RSK-U4-22C-1/2. WIRE ION THE SAME AS IG21.			I&C RACKS

IG23			A "Y" CABLE ASSEMBLY TERMINATING IN TWO CONNECTORS		SSRL			ION-GAU3

WITH 12" LEAD LENGTHS. THE MULTI-CONDUCTOR CABLE		ION GAUGES

IS A BURNDY TT12S AND THE COAX A BNC58.

USE SHRINK-TUBE AT BASE OF "Y".SEE CONNECTORS FOR

PART NUMBERS.

IG24			A "Y" CABLE ASSEMBLY TERMINATING IN TWO CONNECTORS		SSRL			ION-GAU3

WITH 12" LEAD LENGTHS. THE MULTI-CONDUCTOR CABLE		ION GAUGES

IS A BURNDY TT12P AND THE COAX A BNC58.

USE SHRINK-TUBE AT BASE OF "Y".

SEE CONNECTORS FOR PART NUMBERS.

IG-CP6		SIX PIN MALE CABLE PLUG, AMPHENOL CAT-# 86-CP6.						IG-CABLE

IG-RS4		FOUR PIN FEMALE RECEPTACLE, CHASSIS MOUNT, AMPHENOL		VACG (HOT FIL)	ION-GAU2

CAT. #78-RS4 2

IPA			AMPHENOL HV CONNECTOR, 97-5106A-18-420S.				KLY ION PUMP	VARIAN

PRE-WIRED ONTO ONE END OF THE VARIAN HV CABLE

FOR ION PUMPS.

IPL1			COAXIAL CABLE TERMINATION FOR H.V. BOX. SEE DWG. 		DISTRIBUTED		RG213R

AD-208-911-00-RO FOR DETAILS.						ION PUMP

JUNCTION BOX

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

IPL2			COAXIAL CABLE TERMINATION FOR H.V. BOX.				HOLDING ION PUMP	RG213R

SEE DWG. IC7, DETAIL 7. 1 RING LUG,					JUNCTION BOX

AMP NO. 33457 OR EQ. (SLAC S/N59-294-744-51),

1 RING LUG, AMP NO. 31902 OR EQ.

(SLAC S/N59-294-711-41),

AND 1 BUTT CONNECTOR, AMP 320562 OR

EQ. (SLAC S/N59-294-770-07).

IPL3			VARIAN PREFABRICATED ARMORED CABLE TERMINATION			HOLDING ION PUMP	VARIAN A

FOR H.V. BOX. SEE DWG IC7, DETAIL 6,				JUNCTION BOX

AND INSTALL RING LUG WITHOUT SHORTENING

INSULATED INNER WIRE.

IPVA			VARIAN SHIELDED "BANANA PLUG" CONNECTOR FOR			HOLDING ION PUMP	VARIAN,VARIAN A

VAC ION PUMPS, PRE-WIRED ONTO ONE END OF

THE VARIAN HV CABLE FOR ION PUMPS.

IPVA25		VARIAN HV ION PUMP CONNECTOR,						VARIAN HOLDING	TIMES

MODEL 03642700A FOR VAC ION PUMP #25				ION PUMP #25

CONNECTOR MUST BE ASSEMBLED ONTO HV COAX.

IPVB			DUNAWAY STOCK ROOM CORP. TYPE C-100 CONNECTOR FOR		VARIAN HOLDING	RG213

VARIAN HOLDING ION PUMPS.						ION PUMP

IPVC			ION-PUMP CONNECTOR, DESY-TYPE.(XXKV RATED)

MODEL #SR03648982 VARIAN INC. (EXCLUSIVE US.

DISTRIBUTION)STRAIN RELIEF (FOR TYPE-C & RG58R).

195 O.D.REF: CABLE STRAIN RELIEF

SSRL DWG # PF-441-167-40 C0

IPVR			HIGH-VOLTAGE FEED-THRU, DESY-TYPE (XXKV RATED)

DESY FEED-THRU ON MINI-CON FLAT MODEL #SR0364720

IPS100X		VARIAN HV ION PUMP CONNECTOR, FOR VAC ION PUMP			HV ION PUMP		TIMES, TYPE-C

# S100X CONNECTOR	MUST BE ASSEMBLED ONTO HV COAX.

DUNIWAY,PART # S-100-X.

JAE3P			THREE PIN CONNECTOR, MALE PLUG, MFR JAEGER,

DESIGNATOR #FMR G1024, REFERENCE # 532653.

CONNECTOR IS SUPPLIED BY THE ORSAY FACILITY.

JAE3S			THREE PIN CONNECTOR, FEMALE PLUG, MFR JAEGER,

DESIGNATOR #FFR J0086, REFERENCE # 532003.

CONNECTOR IS SUPPLIED BY THE ORSAY FACILITY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

JAE4P			FOUR PIN CONNECTOR, MALE PLUG, MFR JAEGER,

DESIGNATOR #FMR G1003, REFERENCE # 532654.

CONNECTOR IS SUPPLIED BY THE ORSAY FACILITY.

JAE12P		TWELVE PIN CONNECTOR, MALE PLUG, MFR JAEGER,

DESIGNATOR #E6 FMR, REFERENCE # 532662.

CONNECTOR IS SUPPLIED BY THE ORSAY FACILITY.

KST6			CABLE PLUG, SINGLE CONDUCTOR, GERMAN MANUFACTURER,					#6

CONTACT P/N 15-0002-COLOR USED FOR FAST SHUDDER PULSE

CURRENT.

LB01-4		LUG, CRIMP, 1/4" BOLT-HOLE FOR #1/0 AWG WIRE, COPPER					#1/0

LONG BARREL, UNINSULATED, SQUARE-D CAT. #VHCL-1/0-14. USE

SLAC APPROVED CRIMP TOOLING ONLY.

LB01-5		LUG, CRIMP, 5/16-INCH BOLT-HOLE FOR COPPER #1/0 AWG WIRE,				#1/0

WIRE,LONG BARREL, UNINSULATED, SQUARE-D P/N #VHCL 1/0-516.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB01-6		LUG, CRIMP, 3/8-INCH BOLT-HOLE FOR COPPER #1/0 AWG WIRE,				#1/0

LONG BARREL, UNINSULATED, SQUARE-D P/N #VHCL 1/0-38.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB01-6S		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED, STANDARD BARREL.			1/0TLSNH

FOR COPPER #1/0 AWG WIRE OR #1/0 FLEX CABLE. USE MFG T&B

P/N 54109 OR EQUIVALENT. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB01-6SR		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED, STANDARD BARREL,			1/0TLSNH

RIGHT ANGLE.FOR COPPER #1/0 AWG WIRE OR #1/0 FLEX CABLE.

USE MFG T&B P/N 54109UB	OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB01-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE FOR COPPER #1/0 AWG WIRE,				#1/0

LONG BARREL, UNINSULATED, SQUARE-D P/N #VHCL 1/0-12.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB01-8F		LUG, CRIMP, 1/2-INCH BOLT-HOLE FOR COPPER #1/0 AWG 					1/0TLSNH

FLEX CABLE,LONG BARREL.MFG:T&B, P/N:54950BE OR

EQUIVALENT.USE SLAC APPROVED CRIMP TOOLING ONLY.

LB019-6		LUG,CRIMP, 3/8 INCH BOLT HOLE, UNINSULATED,						#1WELD, #1/0

LONG BARREL FOR AL/CU 1/0 CABLE. THOMAS AND BETTS

P/N 60130. USE SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB01D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4 CENTERS.				#1/0

FOR COPPER #1/0 AWG WIRE, LONG BARREL, UNINSULATED, AMP

CAT. #53680-2 USE SLAC-APPROVED CRIMP TOOLING ONLY.

LB02-6		LUG, CRIMP, 3/8-INCH BOLT-HOLE FOR COPPER #2/0 AWG WIRE,				#2/0

LONG BARREL, UNINSULATED, SQUARE-D P/N #VHCL 2/0-38.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB02-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE FOR COPPER #2/0 AWG WIRE,				#2/0

LONG BARREL, UNINSULATED, SQUARE-D P/N #VHCL 2/0-12.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB02D6		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 3/8 DIA ON 1" CENTERS.				#2/0

LONG BARREL, UNINSULATED, FOR COPPER #2/0 AWG WIRE.

SQUARE D P/N #VHCL-2/0-38B.

LB02D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4 CENTERS,				#2/0

FOR COPPER #2/0 AWG WIRE, LONG BARREL, UNINSULATED,

SQUARE-D P/N VHCL- 2/0-12BN USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB03-6		LUG, CRIMP, 3/8-INCH BOLT-HOLE, FOR COPPER #3/0 AWG					#3/0

WIRE, LONG BARREL, UNINSULATED, SQUARE-D

P/N VHCL-3/0-38.USE SLAC APPROVED CRIMP TOOLING ONLY.

LB03-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, FOR COPPER #3/0 AWG WIRE,				#3/0

LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-3/0-12. USE

SLAC APPROVED CRIMP TOOLING ONLY.

LB039-6		LUG,CRIMP, 90 DEGREE, 3/8 INCH BOLT HOLE, UNINSULATED,				2/0WELD, #3/0

LONG BARREL FOR AL/CU 3/0 CABLE. THOMAS AND BETTS

P/N 60142UB. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB049-3		CONNECTOR TERMINAL YELLOW 90 DEGREE STANDARD BARREL					4/0FLX, 4/0TLSNH

#4/0 AWG. 1 HOLE LUG 3/8 INCH BOLT SIZE. ALPHA EQUIPMENT

COMPANY. PART# 58163UB. MANUFACTURER: THOMAS & BETTS.

LB03D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4					#3/0

CENTERS, FOR COPPER #3/0 AWG WIRE, LONG BARREL,

UNINSULATED, SQUARE-D P/N VHCL- 3/0-12BN.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB04-6		LUG, CRIMP, 3/8-INCH BOLT-HOLE, FOR COPPER #4/0 AWG 					#4/0

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-4/0-38.

USE SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB04-6FL		LUG, CRIMP, 3/8-INCH BOLT-HOLE,UNINSULATED,LONG BARREL.				4/0TLSNH

FOR COPPER #4/0 AWG FLEX CABLE.USE MFG T&B P/N:54913BE06

OR EQUIVALENT.USE SLAC APPROVED CRIMP TOOLING ONLY.

LB04-6S		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED, STANDARD BARREL.			4/0TLSNH

FOR COPPER #4/0 AWG FLEX CABLE. USE MFG T&B P/N 54174 OR

EQUIVALENT. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB04-6SR		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED,						4/0TLSNH

STANDARD BARREL,RIGHT ANGLE. FOR COPPER #4/0 AWG FLEX CABLE.

USE MFG T&B P/N 54174UB OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB04-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE FOR COPPER #4/0 AWG					#4/0

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-4/0-12.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB04D6		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 3/8 DIA ON 1" CENTERS.				#4/0

FOR COPPER #4/0 AWG WIRE, LONG BARREL, UNINSULATED,

SQUARE D P/N VHCL-4/0-38B. USE SLAC APPROVED CRIMP TOOLING

ONLY.

LB04D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4 CENTERS,				#4/0

FOR COPPER #4/0 AWG WIRE, LONG BARREL, UNINSULATED,

SQUARE-D P/N VHCL-4/0-12BN. USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB04D8F		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4 CENTERS,				4/0TLSNH

LONG BARREL. FOR COPPER #4/0 AWG FLEX CABLE.

MFG:T&B, P.N: 54868BE. USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB1-4			LUG, CRIMP, 1/4-INCH BOLT HOLE, STANDARD BARREL. FOR COPPER

#1 AWG WIRE. MFG: T&B, P/N:54108 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY

LB1-5			LUG, CRIMP, 5/16-INCH BOLT-HOLE, FOR COPPER #1 AWG					#1

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-1-516.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB1-6			LUG, CRIMP, 3/8-INCH BOLT HOLE, FOR COPPER #1 AWG					#1

WIRE, LONG BARREL, UNINSULATED, SQUARE-D VHCL-1-38.

USE SLAC APPROVED CRIMPING TOOL ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB1-8		   LUG, CRIMP, 1/2-INCH BOLT HOLE, FOR COPPER #1 AWG				    #1

WIRE, STANDARD BARREL, UNINSULATED, MFG: THOMAS & BETTS,

COLOR-KEYED,P/N:54150.

USE SLAC APPROVED CRIMPING TOOL ONLY.

LB1D6			LUG, CRIMP, DOUBLE BOLT HOLE, 2X3/8 DIAMETER ON 1.00"					#1

CENTERS, FOR COPPER #1 AWG WIRE, LONG BARREL,

UNINSULATED, BURNDY P/N YA1C-2TC38. USE SLAC APPROVED

CRIMP TOOLING ONLY.

LB1D8			LUG, CRIMP, DOUBLE BOLT HOLE, 2X1/2 DIAMETER ON 1.75"					#1

CENTERS, FOR COPPER #1 AWG WIRE, LONG BARREL

UNINSULATED, BURNDY P/N YA1C-2N. USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB2SS			LUG, ONE BOLT HOLE, SET SCREW TYPE, FOR #2 TO #4AWG					2/0, 4/0

LB2-4			LUG, CRIMP, 1/4-INCH BOLT-HOLE, FOR COPPER #2 AWG					#2

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-2-14.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB2-5			LUG, CRIMP, 5/16-INCH BOLT-HOLES FOR COPPER #2 AWG,					#2

WIRE, LONG BARREL, UNINSULATED. MFG:T&B, P/N:54942BE

OR EQUIVALENT. (SQUARE-D P/N VHCL-2-516- OBSOLETE).

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB2-6			LUG, CRIMP, 3/8-INCH BOLT-HOLE, FOR COPPER #2 AWG					#2

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-2-38.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB2-6S		Copper One-Hole Lug – Straight Standard Barrel						2C2TLSNH

MAX 35KV, #2 AWG Wire, 3/8” Bolt Mtg Size, Tin Plated

with Inspection Hole, T&B Catalog Number: 54143-TB.

LB2D6			Copper Two-Hole Lug – Straight Long Barrel Max 35KV,					2C2TLSNH

#2 AWG Wire, 3/8” Bolt Mtg Size, 1 3/4” Hole Spacing,

Tin Plated Blind End, Brown 33 T&B Catalog Number: 54810BE.

LB2D8		   DESCRIPTION: COPPER TWO-HOLE LUG - STRAIGHT LONG BARREL			    2C2TLSNH

MAX 35KV, #2 AWG WIRE, 1/2" BOLT MTG SIZE, 1 3/4" HOLE SPACING,		    2C2LSNH

TIN PLATED BLIND END, BROWN 33 T&B CATALOG NUMBER:54811BE

LB25FX6        	LUG, CRIMP, 3/8-INCH BOLT HOLE, UNINSULATED, STANDARD BARREL, 			262FLX

FOR COPPER 262 FLEX DLO CABLE.

MFG: BURNDY. P/N:YA31LTC38FX.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB3/0			LUG, 3/8-INCH COPPER ONE-HOLE FOR #3/0 AWG or 2/0 FLEX WIRE.			2/0TLSNH

STRAIGHT STANDARD BARREL – MAX 35KV. TIN PLATED WITH

INSPECTION HOLE. ORANGE 50. THOMAS&BETTS CATALOG #54111.

LB3D8			LUG, CRIMP, DOUBLE BOLT HOLE, 2 X 1/2IN DIAMETER ON 1-3/4"				2/0TLSNH, 3/0AWG

CENTERS, LONG BARREL, UNINSULATED, FOR COPPER 3/0 AWG WIRE,

THOMAS&BETTS P/N 54864BE.

LB4/0			LUG, CRIMP, 3/8 DIAMETER, STANDARD BARREL, UNINSULATED,				4/0TLSNH

FOR COPPER 4/0 AWG FLEX WIRE, THOMAS&BETTS P/N 58163.

LB4-3			LUG, 1/4-INCH, COPPER ONE-HOLE, FOR #4 AWG WIRE. 					#4,2C4TLN,2C4TLNU

STRAIGHT HOLE. GRAY 29. THOMAS&BETTS CATALOG #54106.

LB4-4			LUG, CRIMP, 1/4-INCH BOLT HOLE, FOR COPPER #2 AWG					#4

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-2-14.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB4-5			LUG, CRIMP, 5/16-INCH BOLT HOLE, FOR COPPER #4 AWG					#4

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-4-516.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB4-6			LUG, CRIMP, 3/8-INCH BOLT HOLE, FOR COPPER #4 AWG					#4

WIRE, LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-4-38.

SLAC S/N59-294-747-81.USE SLAC APPROVED CRIMP TOOLING ONLY.

LB4D8			LUG, CRIMP, DOUBLE BOLT HOLE, 2X1/2 DIAMETER ON 1-3/4"				#4

CENTERS, LONG BARREL, UNINSULATED. FOR COPPER #4 AWG

WIRE. MFG: FCI/BURNDY P/N: #YA4C-2N.

MFG: T&B, P/N: 256-30695-733 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB4-SS		LUG, ONE BOLT HOLE, SET SCREW TYPE, FOR #4 TO #8 AWG.					#4-#8

LB6-3			LUG, CRIMP, #10 BOLT HOLE, FOR COPPER #6 AWG WIRE, LONG				#6

BARREL, UNINSULATED, SQUARE-D P/N VHCL-6-10/8. SLAC

S/N59-294-748-01. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB6-4			LUG, CRIMP, 1/4 INCH BOLT HOLE, FOR COPPER #6 AWG WIRE,				#6

LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-6-14. SLAC

S/N59-294-748-02. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB6-5			LUG, CRIMP, 5/16-INCH BOLT HOLE, FOR COPPER #6 AWG WIRE,				#6

LONG BARREL, UNINSULATED, SQUARE-D P/N VHCL-6-516. USE

SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB6-6			LUG, CRIMP, 3/8-INCH BOLT HOLE, FOR #6 AWG WIRE, SHORT				#6

BARREL, UNINSULATED, AMP CAT. #328144. SLAC

S/N59-294-748-04.  USE SLAC APPROVED CRIMP TOOLING ONLY.

LB6-7			LUG, CRIMP, 1/4-INCH BOLT HOLE, FOR #6 AWG WIRE, SHORT

BARREL, UNINSULATED, GRAINGER #3LL41. DIE CODE 24.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB6D8			LUG, CRIMP, DOUBLE BOLT HOLE, 2X1/2 DIAMETER ON 1-3/4"				#6

CENTERS, LONG BARREL, UNINSULATED, FOR COPPER #6 AWG

WIRE, BURNDY CAT. #YA6C-2N.

LB8/0			LUG, 5/16-INCH, COPPER ONE-HOLE, FOR #8 AWG WIRE. STRAIGHT				2C8TLN

STANDARD BARREL – MAX 35KV, TIN PLATED WITH INSPECTION

HOLE. RED 21. THOMAS&BETTS CATALOG #54131.

LB8-3			LUG, CRIMP, #10 BOLT HOLE, FOR COPPER #8 AWG WIRE, LONG				#8

BARREL, UNINSULATED, BURNDY CAT. #YA8C-TC10.

SLAC S/N59-294-745-51. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB8-4			LUG, CRIMP, 1/4-INCH BOLT HOLE, FOR COPPER #8 AWG WIRE,				#8

LONG BARREL, UNINSULATED, MFG: FCI/BURNDY P/N: #YA8C-TC14.

MFG: T&B, P/N: 54930BE OR EQUIVALENT.

SLAC S/N59-294-745-41. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB8-5			COPPER ONE-HOLE,LUG – STRAIGHT STANDARD BARREL – MAX 35KV,

#8 AWG WIRE, #10 BOLT SIZE, T&B CATALOG NUMBER: 54104

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB8-6			LUG, CRIMP, 3/8-INCH BOLT HOLE, FOR COPPER #8 AWG WIRE,				#8

SHORT BARREL, UNINSULATED, BURNDY CAT. #YA8C-L3-BOX. USE

SLAC APPROVED CRIMP TOOLING ONLY.

LB8-8			LUG, CRIMP, 1/2-INCH BOLT HOLE, FOR COPPER #8 AWG WIRE,				#8

SHORT BARREL, UNINSULATED, BRUNDY CAT. #YA8C-L4-BOX. USE

SLAC APPROVED CRIMP TOOLING ONLY

LB8-SS		LUG, ONE BOLT HOLE, SET SCREW TYPE, FOR #14 TO #8 AWG.				#14-#8

LB25-6		LUG, CRIMP, 3/8-INCH BOLT HOLE, UNINSULATED, LONG BARREL,				250MCM

FOR COPPER 250MCM CABLE, SQUARE-D P/N VHCL-250-38. USE

SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB25-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED,						250MCM

LONG BARREL, FOR COPPER 250MCM CABLE.

SQUARE-D P/N VHCL-350-12. USE SLAC APPROVED

CRIMP TOOLING ONLY.

LB25D8		LUG, CRIMP, DOUBLE BOLT HOLE, 2 X 1/2IN DIAMETER ON 1-3/4"				4/0TLSNH,250MCM

CENTERS, LONG BARREL, UNINSULATED, FOR COPPER 250MCM WIRE,

THOMAS&BETTS P/N 54868BE

LB30-6		LUG, CRIMP, 3/8-INCH BOLT HOLE, UNINSULATED,						300MCM

LONG BARREL, FOR AL/CU 300MCM CABLE, THOMAS

AND BETTS P/N 60160. USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB30D6		LUG, CRIMP, DOUBLE BOLT HOLE, 2X 3/8" DIA							300MCM

ON 1-3/4 CENTERS. UNINSULATED, LONG BARREL,

FOR 300MCM COPPER CABLE, SQUARE-D P/N VHCL-300-38BN.

USE SLAC APPROVED CRIMP	TOOLING ONLY.

LB30D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA							300MCM

ON 1-3/4 CENTERS. UNINSULATED, LONG BARREL,

FOR 300 MCM COPPER CABLE. SQUARE-D

P/N VHCL-300-12BN. USE SLAC APPROVED CRIMP

TOOLING ONLY.

LB35-5FS		LUG, CRIMP, 5/16-INCH BOLT – SINGLE HOLE,UNINSULATED,

SHORT BARREL. FOR COPPER 350 MCM FLEX CABLE.

PANDUIT CAT.#LCAX350-56-6 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35-6FL		LUG, CRIMP, 3/8-INCH BOLT - SINGLE HOLE, UNINSULATED,					350TLSNH

LONG BARREL. FOR COPPER 350 MCM FLEX CABLE. T&B

CAT.# 54916BE06 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35-6FS		LUG, CRIMP, 3/8-INCH BOLT - SINGLE HOLE, UNINSULATED,					350TLSNH

SHORT BARREL. FOR COPPER 350 MCM FLEX CABLE.

T&B CAT.# 5411606 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED,						350MCM

LONG BARREL, FOR COPPER 350 MCM CABLE. SQUARE-D

P/N VHCL-350-12. USE SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB35-9		LUG, CRIMP, 3/8-INCH BOLT - SINGLE HOLE, UNINSULATED,					350TLSNH

SHORT BARREL, FOR COPPER 350 MCM FLEX CABLE. T&B

CAT. # 256-30695-112 USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35-10		LUG, CRIMP, 3/8-INCH BOLT - DOUBLE HOLE, 2 X 3/8" DIA 				350TLSNH

ON 1" CENTERS, UNINSULATED, LONG BARREL, FOR COPPER

350MCM FLEX CABLE (ALSO GOOD FOR 313 FLEX AND 400MCM CODE)

USE T&B TOOL  TBM8-750M-1 WITH BLUE DIE CODE # 76 OR SLAC

APPROVED CRIMP TOOLING ONLY. T&B CAT. # 54821BE313BS.

LB35D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON						350MCM

1-3/4 CENTERS. UNINSULATED, LONG BARREL, FOR 350 MCM

COPPER CABLE. SQUARE-D P/N VHCL-350-12BN.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35D8F		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON						350TLSNH

1-3/4 CENTERS, LONG BARREL. FOR COPPER 350 MCM

FLEX CABLE. MFG: T&B, P/N:54874BE OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35D8FS		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2" DIA ON 1-3/4" CENTERS,			350TLSNH

UNINSULATED, STANDARD  BARREL. FOR 350 MCM FLEXIBLE COPPER

CABLE T&B CAT. # 58277 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB35D9		LUG,CRIMP,DOUBLE BOLT-HOLE, 2 X 1/2" DIA ON 1-3/4"

CENTERS.UNINSULATED, LONG BARREL, FOR 350 MCM FLEXIBLE

COPPER CABLE(ALSO GOOD FOR 313 MCM FLEX AND 400MCM CODE)

T&B CAT. #5487BE313BS. USE T&B TOOL TBM8-750M-1 WITH BLUE

DIE CODE # 76 OR SLAC APPROVED C CRIMP TOOLING ONLY.

LB50-6		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED, STANDARD BARREL,			500MCM

FOR COPPER 500MCM CABLE. USE SLAC APPROVED CRIMP TOOLING ONLY.

MFG: THOMAS & BETTS. P/N 256-30695-339

LB50-6F		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED, STANDARD BARREL.			500TLSNH

FOR COPPER 500MCM FLEX CABLE. USE MFG T&B P/N 5412006 OR

EQUIVALENT. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB50-6FL		LUG, CRIMP, 3/8-INCH BOLT-HOLE, UNINSULATED,						500TLSNH

LONG BARREL. FOR COPPER 500MCM FLEX CABLE. USE MFG

T&B P/N 54921BE06 OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB50-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED,						500MCM

SHORT BARREL,FOR COPPER 500-600 MCM CABLE.

SQUARE-D P/N VHCL-500-12.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB50D6		LUG, CRIMP, 2 BOLT HOLES, 3/8" DIAMETER ON 1"

CENTERS, LONG BARREL, UNINSULATED, FOR 450

TO 550 MCM CABLE. AMP CAT. #326808.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB50D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA							500MCM

ON 1-3/4 CENTERS, LONG BARREL, UNINSULATED,

FOR COPPER 450-550 MCM CABLE.	AMP CAT.#53642-2.

USE SLAC-APPROVED CRIMP TOOLING ONLY.

LB50D8F		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA							500TLSNH

ON 1-3/4 CENTERS, LONG BARREL, FOR COPPER

500 MCM FLEX CABLE. MFG: T&B, P/N:54878BE OR

EQUIVALENT.USE SLAC-APPROVED CRIMP TOOLING ONLY.

LB50D8FS		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA ON 1-3/4 CENTERS,				500TLSNH

STANDARD BARREL. FOR COPPER MCM FLEX CABLE, USE MFG: T&B,

P/N: 54289BE OR EQUIVALENT.

USE SLAC APPROVED CRIMP TOOLING ONLY.

LB53D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA							535MCM

ON 1-3/4 CENTERS, LONG BARREL, UNINSULATED,

FOR COPPER 535KCMIL CABLE.SQUARE-D

P/N VHCL-535-12. USE SLAC-APPROVED CRIMP TOOLING ONLY.

LB60-5		LUG, CRIMP, 5/8-INCH BOLT-HOLE, UNINSULATED, STANDARD 				600MCM,500TLSNH

BARREL,600MCM FOR COPPER 600 MCM CABLE , 5002AND 500MCM 				2C500TLS

FLEX CABLE.T&B PART 500TLSNH NUMBER 54120, TIN PLATED

BLIND END, GREEN 94 OR SLAC APPROVED CRIMP TOOLING ONLY.

LB60-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED, LONG BARREL,				600MCM, 500TLSNH

FOR COPPER 600 MCM CABLE AND 500MCM FLEX CABLE. T&B PART

NUMBER 54921BE, TIN PLATED BLIND END, GREEN 94

LB60D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA.						600MCM

ON 1-3/4 CENTERS. UNINSULATED, LONG BARREL

FOR 600 MCM COPPER CABLE. SQUARE-D P/N VHCL-600-12BN.

USE SLAC-APPROVED CRIMP TOOLING ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LB60S8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED, SHORT BARREL,				600MCM, 500TLSNH

FOR COPPER 600 MCM COPPER CABLE, AND 500MCM FLEX CABLE.

T&B PART NUMBER 256-30695-1370

LB75-8		LUG, CRIMP, 1/2-INCH BOLT-HOLE, UNINSULATED,						750MCM

LONG BARREL,FOR COPPER 750 MCM CABLE.

BURNDY CAT. #YA39-N. USE SLAC APPROVED CRIMP TOOLING ONLY.

LB75D8		LUG, CRIMP, DOUBLE BOLT-HOLE, 2 X 1/2 DIA							750MCM

ON 1-3/4 CENTERS. UNINSULATED, LONG BARREL,

FOR 750MCM COPPER CABLE. SQUARE-D VHCL-750-12BN.

USE SLAC-APPROVED CRIMP TOOLING ONLY.

LB309-6		LUG,CRIMP, 90 DEGREE, 3/8 INCH BOLT HOLE,							250WELD,300MCM

UNINSULATED,LONG BARREL FOR AL/CU 300MCM CABLE.

THOMAS AND BETTS P/N 60160UB. USE SLAC APPROVED

CRIMP TOOLING ONLY.

LBR02-6		LUG, CRIMP, RIGHT ANGLE, 3/8-INCH BOLT-HOLE FOR COPPER				#1/0FLEX, #2/0

#2/0 AWG AND #1/0 AWG FLEX WIRE. STANDARD BARREL,

UNINSULATED,THOMAS&BETTS P/N 54110UB. USE SLAC APPROVED

CRIMP TOOLING ONLY.

LC			CONNECTOR IS FACTORY TERMINATED WITH A LC/UPC CONNECTOR

AND A 1 m PIGTAIL WHICH IS UNTERMINATED. THE PIGTAILS ARE

SINGLE MODE FIBER AND COLOR CODED TO STANDARD EIA/TIA COLOR

SCHEMA. WHEN USED WITH THE COMMSCOPE SYSTIMAX G2 SHELF

SYSTEM THE LC PIGTAILS ARE PART OF A 12 CONNECTOR MODULE:

SYSTIMAX P/N MODG2-12LC-SM.

LC-DUP		FIBER OPTIC CONNECTOR, DUPLEX, 2 FIBER CABLE, 900μm					FOMMDP62

tight-buffered cable recommended 62.5/125μm OM1,

50/125μm OM2, 10GIG™ 50/125μm laser optimized OM3

and 9/125μm OS1, 1.6mm – 2.0mm jacketed cable, Panduit

P/N FLCDMEI (multimode with 1.6mm – 2.0mm jacketed cable),

P/N FLCDM900EI (900μm buffered fiber), P/N FLCDSBU

(singlemode with 1.6mm – 2.0mm jacketed cable), P/N

FLCDS900BU(singlemode with 900μm buffered fiber).

LC-SIM		FIBER OPTIC CONNECTOR, SIMPLEX SINGLE FIBER CONNECTOR,

900μm tight-buffered cable recommended 62.5/125μm OM1,

50/125μm OM2, 10GIG™ 50/125μm laser optimized OM3 and

9/125μm OS1, 1.6mm 2.0mm jacketed cable Panduit P/N

FLCSMEI(multimode), P/N FLCSSBU (singlemode with 900μm

buffered fiber and 1.6mm – 2.0mm jacketed cable)

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LEMO			CONNECTOR, COAXIAL PLUG, KINGS CAT.#1075-1,						RG174, RG188

SLAC S/N59-299-052-01. USE CRIMP DIE KTH-2082.

LEMO-A		USE LEMO2P CONNECTOR.

WIRE #1 WIRE (CLEAR) TO THE SOCKET-PIN (PIN-2).						2C22MS

WIRE #2 WIRE (BLACK) TO THE PLUG-PIN (PIN-1).

WIRE SHIELD TO CONNECTOR SHELL.

LEMOHV1		   CONNECTOR, COAXIAL PLUG, HIGH VOLTAGE (HV), CABLE SIZE O.D.		    RG58TLN

2.2MM - 2.6MM (0.09IN - 0.1IN), 7500 VAC/10500 VDC, 8 AMP

AC/DC, 250 DEG C. LEMO P/N:FFB.1S.405.CTAC27.

LEMOHV2		   CONNECTOR, COAXIAL PLUG, HIGH VOLTAGE (HV), CABLE SIZE O.D.		    TYPE-C

4.3MM - 5.1MM (0.17IN - 0.2IN), 7500 VAC/10500 VDC, 8 AMP

AC/DC, 250 DEG C.LEMO P/N:FFB.1S.405.CLAC52.

LEMO2P		CONNECTOR, LEMO TYPE, KINGS, K-LOC, 2 CONTACT						2C22MS, RG108A

CABLE PLUG, SOLDER CUPS, KINGS #1885-1,

SLAC S/N59-299-053-52.

LEMO3P		   THREE PIN CONNECTOR,  PLUG, 3 CONTACTS (2 PINS AND 1 SOCKET),

HALF MOON INSERT ARRANGEMENT, SOLDER CUP, CABLE O.D.

RANGE: 4.8-5.6MM MFG: LEMO, P/N:FFA.1S.303.CLAC57

LEMO4P		CONNECTOR, LEMO TYPE, KINGS, K-LOC, 4 CONTACT 						1PR20OS

CABLE PLUG, SOLDER CUPS, KINGS #1905-1,

SLAC S/N59-299-053-54.

LEMO5P		FIVE PIN CONNECTOR, MALE PLUG. POWER PLUG FOR ROPER

SCIENTIFIC CAMERA MODEL: CASCADE 512B. MFG: LEMO.

LEMO6P		CONNECTOR, LEMO TYPE, 6 CONTACT CABLE PLUG,

SOLDER CUPS, P/N FFA.1S.306.CLAD.62 PIN ALIGNED

LEMO6PK		CONNECTOR, LEMO TYPE, 6 CONTACT CABLE PLUG,

SOLDER CUPS, KEYWAY ALIGNED, P/N FGG.1B.306.CLAD.72Z.

USE BEND RELIEF BOOT P/N GMA.1B.065.D (BLACK BOOT).

LEMO8PK		CONNECTOR, LEMO TYPE, 8 CONTACT CABLE PLUG,

SOLDER CUPS, P/N FGG.2B.308.CLAD.99Z KEYWAY ALIGNED.

LEMO58		CONNECTOR, COAXIAL PLUG, KING K-LOC, KING CAT #1075-2.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LFB			LUG, "FASTON", BLUE PREINSULATED CRIMP				CROSS-CONNECT	(nn)C16 SERIES,

RECEPTACLE FOR #14 TO, #16 AWG WIRE,				TERMINAL BLOCKS	3PR22OS, 4PR18TC,

AMP CAT. #42332-2. SLAC S/N59-294-751-02,				TRUNKS		24PR16TC, 50PR16TC,

USE HAND CRIMPING TOOL AMP #59250.								3C16TYR, 5PR20OS,

1PR16T3V, 4PR16AS,

5C16,6V, 8PR16OS,

6C18TC,12C18OS,

18PR22OS,50C16T3V,

2C16T3V

LFR			LUG, "FASTON", FEMALE, RED PREINSULATED CRIMP			FLOW & LIMIT	12C22T6V, 15PR22OS,

RECEPTACLE FOR #18 TO #22 AWG WIRE, AMP 				SWITCHES		26C22/3V, 1PR22OS,

CAT. NO.42599-2. SLAC S/N59-294-751-01.							27PR22OS, 2C22MS,

USE HAND CRIMPING TOOL AMP #59250 ONLY.							3PR22OS, 2C16OS,

5PR20OS, 6PR22OS,

19C16T6V, 11PR22OS,

5C16T6V, 8C18OS,

19C18T3V, 9C18J,

18PR22OS, 2C18TC,

5C18TC, 6C18TC,

7C18TC, 12C18TC,

19PR22IS, 12C20J

4C20OS, 12PR22IS,

4PR18TC, 4C20OS,

LF-RA			LUG FASTON, RIGHT ANGLE, SPECIAL ASSEMBLY, FLAG

TERMINALS. MFG. ELPRESS P/N'S B2507 FLPB8 AND B1003

FLSV5. ASSEMBLED WITH ISOLATORER.

LFY			LUG, "FASTON", YELLOW PREINSULATED RECEPTACLE			AC LINE		3C12TYR, 2C12TYR

FOR #12 TO #10 AWG WIRE, AMP CAT. NO. 42844-1. SLAC 					5C12TYR

S/N59-294-751-03. USE HAND CRIMPING TOOL 90246-1 ONLY.

LOPWR21		PLUG CONNECTOR, FEMALE, COAX STYLE, LOW DC POWER. 2.1MM ID,

5.5MM OD. SUPPLIER: DIGIKEY. MFG: CUI. P/N: PP3-002A.

LRB1/4		LUG, RING, BLUE, CRIMP, STUD SIZE 1/4", FOR #14 TO

#16 AWG WIRE. AMP CAT. #31906 OR EQUIVALENT, SLAC

S/N59-294-711-61. USE HAND CRIMPING TOOL 90009-8.

LRB3/8		LUG, RING, BLUE, CRIMP, STUD SIZE 3/8" FOR #14 TO #16					1PR16OS

AWG WIRE, SLAC S/N59-294-711-81. USE HAND CRIMPING

TOOL AMP#59250.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LRB#6			LUG, RING, BLUE, CRIMP, STUD SIZE #6, FOR #14 TO #16 AWG	BACKLEGS		2C14TYR, 1PR16OS

WIRE. AMP NO. 31901 OR EQUIVALENT, SLAC							8C16/3V, 8PR16TS

S/N59-294-711-31.	USE HAND CRIMPING TOOL AMP #59250.					4PR16OS

WIRE IN COLOR CODE SEQUENCE. SEE THE WIRE TYPE FOR THE

COLOR CODE.

LRB#8			LUG, RING, BLUE, CRIMP, STUD SIZE #8, FOR #14 TO #16					2C16/3V

AWG WIRE.AMP 31902 OR EQUIVALENT, SLAC S/N59-294-711-41.

USE HAND CRIMPING TOOL AMP #59250.

LRB#10		LUG, RING, BLUE, CRIMP, STUD SIZE #10, FOR #14 TO #16					4PR16AS

AWG WIRE. AMP 31903 OR EQUIVALENT, SLAC S/N59-294-711-51.

USE HAND CRIMPING TOOL AMP #59250.

LRR1/4		LUG, RING, RED, CRIMP, STUD SIZE 1/4", FOR #18 TO					1PR20OS, 12PR22IS

#22 AWG WIRE. AMP 31894 OR EQUIVALENT, SLAC						12C22/3V

S/N 59-294-710-61.USE HAND CRIMPING TOOL AMP #59250.

LRR#6			LUG, RING, RED, CRIMP, STUD SIZE #6, FOR #18 TO #22 AWG				1PR20OS

WIRE. AMP 8-36152-1 OR EQUIVALENT, SLAC S/N59-294-710-31.

USE HAND CRIMPING TOOL AMP #59250.

LRR#8			LUG, RING, RED, CRIMP, STUD SIZE #8, FOR #18 TO #22 AWG

WIRE. AMP 31890 OR EQUIVALENT. SLAC P/N59-294-710-41. USE

HAND CRIMPING TOOL AMP #59250.

LRY6R			LUG, RING, YELLOW, CRIMP, STUD SIZE #6, FOR #10 TO #12 AWG				2C12TYR, 2C10TC

WIRE. RADIATION RESISTANT INSULATION (PVF2), BURNDY CAT.				4C12T6V, 4C1076V

#YAES10K-11. USE HAND CRIMP TOOL AMP #59239-4.

LRY#6			LUG, RING, YELLOW, CRIMP, STUD SIZE #6, FOR #10 TO #12 AWG		AC POWER	3C12TYR, 2C12OS

WIRE. AMP NO. 35149 OR EQUIVALENT, LBL #5940-3194, SLAC

S/N59-294-713-31.USE HAND CRIMPING TOOL AMP #59239-4.

WIRE IN COLOR CODE SEQUENCE. SEE THE WIRE TYPE FOR THE

COLOR CODE.

LRY#6-1		LUG, RING, YELLOW, CRIMP, STUD SIZE #6, FOR #16 TO #14				8C12T6V

AWG WIRE. AMP NO. 35634 OR EQUIVALENT, SLAC

S/N59-294-712-31.USE HAND CRIMPING TOOL AMP #59239-4.

LRY-7			LUG RING TONGUE, YELLOW, INSULATED, CRIMP, STUD SIZE #6,

FOR #10 OR #12 AWG WIRE. COPPER LUG WITH 0.145 DIA HOLE.

AMP CAT# 320634, USE HAND CRIMPING TOOL AMP #59239-4.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LRY#8			LUG, RING, YELLOW, CRIMP, STUD SIZE #8, FOR #10						5C12TYR, 2C12TYR

TO #12 AWG WIRE. AMP 35108 OR EQUIVALENT,

SLAC59-294-713-41. USE HAND CRIMPING TOOL AMP #59239-4.

LRY#8-1		LUG, RING, YELLOW, CRIMP, STUD SIZE #8, FOR #16 					8C12T6V

TO #14 AWG WIRE. AMP 35106 OR EQUIVALENT,

SLAC59-294-712-41. USE HAND CRIMPING TOOL AMP #59239-4.

LRY#10		LUG, RING, YELLOW, CRIMP, STUD SIZE #10, FOR #10					3C12TYR, 4C12TYR

TO #12 AWG WIRE. AMP 35109 OR EQUIVALENT, SLAC

S/N59-294-713-51. USE HAND CRIMPING TOOL AMP #59239-4.

LRY#10-1		LUG, RING, YELLOW, CRIMP, STUD SIZE #10, FOR #16 TO #14				8C12T6V

AWG WIRE. AMP 34805 OR EQUIVALENT, SLAC S/N59-294-712-51.

USE HAND CRIMPING TOOL AMP #59239-4.

LRY1/4		LUG, RING, YELLOW, CRIMP, FOR 1/4" STUD SIZE, FOR					#12

#10 TO #12 AWG WIRE. SLAC S/N59-294-713-61.

USE HAND CRIMP TOOL AMP #59239-4.

LRY-5			LUG RING, YELLOW, INSULATED, CRIMP, STUD SIZE 5/16",					#12

FOR #10 OR #12 AWG WIRE. AMP CAT. #35111, SLAC

59-294-713-71.USE HAND CRIMPING TOOL AMP #59239-4.

LRY-6			LUG RING, YELLOW, INSULATED, CRIMP, STUD SIZE 3/8",					#12

FOR #10 OR #12 AWG WIRE. AMP CAT# 35112,

SLAC S/N59-294-713-81. USE HAND CRIMPING TOOL

AMP #59239-4.

LRY-8			LUG RING, YELLOW, INSULATED, CRIMP, STUD SIZE 1/2",					#12

FOR #10 OR #12 AWG WIRE. AMP CAT# 35151,

SLAC S/N59-294-713-91. USE HAND CRIMPING TOOL

AMP #59239-4.

LR2-5			LUG, RING, UNINSULATED, CRIMP, STUD SIZE 5/16", FOR #2 				#2

AWG WIRE, AMP CAT. #322870 OR EQUIVALENT. USE SLAC

APPROVED CRIMPING TOOL ONLY.

LR2-6			LUG, RING, UNINSULATED, CRIMP, STUD SIZE 3/8", FOR					#2

#2 AWG WIRE, AMP CAT. #321600. USE SLAC

APPROVED CRIMPING TOOL ONLY.

LR2-8			LUG, RING, UNINSULATED, CRIMP, STUD SIZE 1/2", FOR					#2

#2 AWG WIRE, AMP #321602 OR EQUIVALENT. USE SLAC APPROVED

CRIMPING TOOL ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LR4#10		LUG, RING, INSULATED, CRIMP, STUD SIZE #10, FOR #4 					#4

AWG WIRE,AMP CAT. #322052. USE SLAC APPROVED

CRIMPING TOOL ONLY.

LR6#10		LUG, RING, UNINSULATED, CRIMP, STUD SIZE #10,			FF KICKER		#6,HVSPEC1

FOR #6 AWG WIRE.AMP CAT. #33464. USE SLAC APPROVED

CRIMPING TOOL ONLY.

LR6#10S		LUG,RING,UNINSULATED,CRIMP,FOR #6AWG,STUD SIZE			TRIM WINDING	2C6T6VOS

#10,19 STRAND WIRE, AMP 321298, USED SLAC APPROVED

CRIMPING TOOL ONLY.

LR8-4			LUG, RING,INSULATED, CRIMP, STUD SIZE 1/4", FOR #8

AWG WIRE, AMP CAT. #33461, SLAC S/N59-294-745-41.

USE SLAC APPROVED CRIMPING TOOL ONLY.

LR8-6			LUG, RING, INSULATED, STUD SIZE 3/8 INCH, FOR #8		FF			2C8TYR

AWG WIRE,AMP CAT. #322004. USE SLAC APPROVED CRIMPING

TOOL ONLY.

LR8#10		LUG, RING, INSULATED, CRIMP, STUD SIZE #10, FOR #8 AWG				4C8TYR,4C8SHLD

WIRE, AMP CAT. #322154,SLAC S/N59-294-745-51. USE SLAC

APPROVED CRIMPING TOOL ONLY.

LR8U10		LUG, RING, UNINSULATED, CRIMP, STUD SIZE #10, FOR #8 AWG	FOCUS MAG		#8

WIRE. AMP. CAT #31807, SLAC S/N 59-294-745-51. USE SLAC

APPROVED CRIMPING TOOL ONLY.

LSB#6			LUG, SPADE, BLUE, CRIMP, STUD SIZE #6, FOR #14 TO #16 AWG				3C16TYR, 1PR16AS,

WIRE. AMP #320861 OR EQUIVALENT, LBL #5940-31964, SLAC				4PR16AS, 1PR16T3V,

S/N59-294-733-31. USE HAND CRIMPING TOOL AMP #59250.					2C16/3V, 5C16/6V,

9C18J

LSB#8			LUG, SPADE, BLUE, CRIMP, STUD SIZE #8, FOR #14 TO #16 AWG				2C16OS, 3C16/3V

WIRE. AMP NO. 320862 OR EQUIVALENT, LBL #5940-31989, SLAC

S/N59-294-733-41. USE HAND CRIMPING TOOL AMP #59250.

LSB#10		LUG, SPADE, BLUE, CRIMP, STUD SIZE #10, FOR #14 TO #16

AWG WIRE. AMP NO.320863 OR EQUIVALENT, SLAC

S/N59-294-733-51. USE HAND CRIMPING TOOL AMP #59250.

LSR#6			LUG, SPADE, RED, CRIMP, STUD SIZE #6, FOR #18 TO					2C22MS, 12C18OS,

#22 AWG WIRE. AMP NO. 32562 OR EQUIVALENT, LBL						2C18TC, 6C18TC,

#5940-31951, SLAC S/N59-294-732-31. USE HAND						8C18OS

CRIMPING TOOL AMP #59250.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

LSR#8			LUG, SPADE, RED, CRIMP, STUD SIZE #8, FOR #18 TO

#22 AWG WIRE. AMP NO.32498 OR EQUIVALENT,

SLAC S/N59-294-732-41. USE HAND CRIMPING TOOL

AMP #59250.

LSR#10		LUG, SPADE, RED, CRIMP, STUD SIZE #10, FOR #18 TO

#22 AWG WIRE. AMP NO.32054 OR EQUIVALENT, SLAC

S/N59-294-722-51.	USE HAND CRIMPING TOOL AMP #59250.

LSY#8			LUG, SPADE, YELLOW, CRIMP, STUD SIZE #8, FOR #10					2C12TYR, 2C10TYR,

TO #12 AWG WIRE.AMP 32510 OR EQUIVALENT.							HVSPEC2

SLAC S/N59-294-735-41.USE HAND CRIMPING TOOL 59239-4 ONLY.

LSY#10		LUG, SPADE, YELLOW, CRIMP, STUD SIZE #10, FOR

#10 TO #12 AWG WIRE. AMP NO. 32589 OR EQUIVALENT,

USE HAND CRIMPING TOOL 90246-1 ONLY.

MCX			BANANA TYPE PLUG WITH WHITE COLORED PLASTIC						KAPTON

INSULATING SHELL FURNISHED WITH THE KAPTON CABLE TYPE.

MG8P			EIGHT PIN CONNECTOR, MALE, CABLE PLUG,							4PR22IS

MFR. MELLES GRIAT P/N 06DDA002.

MG8S			EIGHT PIN CONNECTOR, FEMALE, CABLE PLUG,							4PR22IS

MFR. MELLES GRIAT P/N 06DDA001.

MLP			CONNECTOR, MALE, CABLE PLUG, 90 AMP, MULTILAM HUGIN					#4AWG

INDUSTRIES P/N 09043.

MLS			CONNECTOR, FEMALE, CABLE SOCKET, 90 AMP, MULTILAM 					#4AWG

HUGIN INDUSTRIES P/N 10751.

MLX3S			CONNECTOR, 3 PIN, FEMALE, SOLDER CONNECTIONS. MOLEX P/N

09-50-3061.

MLX4P			FOUR PIN CONNECTOR, MOLEX CAT. #39-01-2045, WITH

CONTACT POINT AND STRAIN RELIEF, MOLEX CAT.#39-00-0220

AND 15-04-0296 RESP.

MLX4S			FOUR PIN CONNECTOR, FEMALE RECEPTACLE, MOLEX CAT.					1PR18OS

#39-01-2040, STRAIN RELIEF, MOLEX CAT. #15-04-0294

AND GOLD PLATED TERMINALS, MOLEX CAT. #39-00-164.

USE HAND CRIMPING TOOL, MOLEX CAT. #11-01-0197.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MLX4X			FOUR PIN CABLE CONNECTOR, MOLEX CAT#39-01-3049,

WITH CONTACT POINT AND STRAIN RELIEF,

MOLEX CAT.#39-00-0182 AND 15-04-0296 RESP.

THIS SHALL BE USED TO DISCONNECT THE CABLE WHEN THE

RAFT IS MOVED AWAY FROM THE DETECTOR.

MLX6S			SIX PIN CONNECTOR, FEMALE RECEPTACLE, MOLEX CAT.					2PR18OS

#39-01-2060, STRAIN RELIEF, MOLEX CAT. #15-04-0296

AND GOLD PLATED TERMINALS, MOLEX CAT. #39-00-164.

USE HAND CRIMPING TOOL, MOLEX CAT. #11-01-0197.

MLX6S1		SIX PIN CABLE CONNECTOR, MOLEX CAT. #39-01-2065, WITH

CONTACT POINT AND STRAIN RELIEF, MOLEX CAT. #39-00-0220

AND 15-04-0296 RESP.

MLX12P		TWELVE PIN CABLE CONNECTOR, MOLEX CAT. #39-01-2125,

WITH CONTACT POINT AND STRAIN RELIEF, MOLEX CAT.

#39-00-0220	AND 15-04-0345 RESP.

MLX12S		TWELVE PIN CONNECTOR, FEMALE RECEPTACLE, MOLEX						4PR18OS, 1PR18OS

CAT. #39-01-2120, STRAIN RELIEF, MOLEX CAT. #15-04-0345

AND GOLD PLATED TERMINALS, MOLEX CAT. #39-00-164.

USE HAND CRIMPING TOOL, MOLEX CAT. #11-01-0197

AND #39-01-2125.

MLX12X		TWELVE PIN CABLE CONNECTOR, MOLEX CAT. #39-01-3129,

WITH CONTACT POINT AND STRAIN RELIEF, MOLEX CAT.#39-00-0182

AND 15-04-0345 RESP. THIS SHALL BE USED TO DISCONNECT THE

CABLE WHEN THE RAFT IS MOVED AWAY FROM THE DETECTOR.

MS-HVS		SINGLE CONTACT, THREADED CONNECTOR, AMPHENOL						RG213R

NO. MS-3106A-18-420S, RATED AT 9 KV RMS/20 A MAX.

TERMINATION IS TO BE DONE PER DRAWING SA-125-089-01,

'ION PUMP HV CABLE CONNECTOR ASSEMBLY'.

MS2S			TWO PIN CONNECTOR, FEMALE STRAIGHT PLUG,ITT 						1PR22OS

CANNON P/N MS3106A-12S-3S. SOLDER PINS

MS3P			THREE PIN CONNECTOR, MALE, MS-3126F-12-3P, SLAC			TUNE MEAS		2C22MS, 2C16OS

S/N 59-299-210-52. USE HAND CRIMPING TOOL M10S-1

WITH DIE S-7 AND STOP SL-2 ONLY.

MS3S			THREE PIN CONNECTOR, FEMALE, MS-3126F-12-3S, 			TUNE MEAS		2C22MS, 3C20/3V

SLAC S/N59-299-210-02. USE HAND CRIMPING TOOL 						1PR22OS

M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS3S-A		THREE PIN CONNECTOR, FEMALE, MS3106A-10SL-3S, 						8PR22OS

STRAIGHT PLUG, SOLDER CONNECTIONS, MFR IS AMPHANOL.

NOT A SLAC STORES ITEM.

MS3S-S		THREE PIN CONNECTOR, FEMALE, MS-3106B-14S-7S,			LINAC VAC		1PR22OS

STRAIGHT PLUG, SPLIT SHELL, SOLDER CONNECTIONS,

MFR. AMPHENOL. NOT  SLAC STORES ITEM.

MS4P			FOUR PIN CONNECTOR, MALE, BENDIX P/N PTO6A-8-4P.

MS4S			FOUR PIN CONNECTOR, FEMALE, BENDIX P/N PTO6A-8-4S.

MS4SA			FOUR PIN CONNECTOR, FEMALE, MS-3116F-8-4S.			SLMO			1PR22OS

MS5P			FIVE PIN CONNECTOR, MALE, MS3126F-14-50, SLAC 			FF KICKER		6C16OS

P/N 59-299-210-54. USE HAND CRIMPING TOOL

MS10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS5S			FIVE PIN CONNECTOR, FEMALE, MS-3126F-14-5S, SLAC		KLY AMP		3C16/3V, HVSPEC2

S/N59-299-210-04. USE HAND CRIMPING TOOL 				FF KICKER		6C16OS

M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS5SR			FIVE PIN CONNECTOR, FEMALE RECEPTACLE, 							2PR22OS

MS-3120E-14-5S. USE HAND CRIMPING TOOL MS10S-1

WITH DIE S-7 AND STOP SL-2 ONLY.

SLAC S/N59-299-410-54.

MS5S-S		FIVE PIN CONNECTOR, MS3106A-18-11S, STRAIGHT PLUG,		KLY/KICKER		#10AWG

FEMALE, SOLDER CONNECTIONS, MFR-AMPHENOL.

NOT A SLAC STORES	ITEM.

MS6P			SIX PIN CONNECTOR, MALE, MS-3126F-10-6P,

SLAC P/N59-299-210-51. USE HAND CRIMPING TOOL

M10S-1 WITH DIE S-6A AND STOP SL-3A	ONLY.

MS6PR			SIX PIN MALE CHASSIS MOUNT CONNECTOR, MS-3120-10-6P,

SLAC P/N59-299-410-01. USE HAND CRIMPING TOOL M10S-1

WITH DIE S-6A AND STOP SL-3A ONLY.

MS6PRC		SIX PIN CONNECTOR, MALE, CABLE END RECEPTACLE,

MS-3121F-10-6P. USE HAND CRIMPING TOOL M10S-1 WITH

DIE S-6A AND STOP SL-3A ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS6PSB		SIX PIN CONNECTOR, MALE, MS-3126F-10-6P, S/N			CAMAC SERIAL	3PR24IS

59-299-210-51. USE HAND CRIMPING TOOL M10S-1			BRANCH CABLE

WITH DIE S-6A AND STOP SL-3A ONLY. WIRE PER

DRAWING CA-123-854-00:

PAIR 1, BLACK/RED,	RED TO PIN-A

W/DRAIN		BLACK TO PIN-B

PAIR 2, BLACK/GREEN,	GREEN TO PIN-C

W/DRAIN		BLACK TO PIN-D

DRAIN WIRES, PAIRS 1 & 2, CONNECT BOTH TO PIN-E

NO CONNECTION TO PIN-F.

PAIR 3, BLACK/WHITE,	NO CONNECTIONS,

CUT BACK TO EDGE OF JACKET.

MS6S			SIX PIN CONNECTOR, FEMALE, MS-3126F-10-6S. SLAC 		DC XFMR		3PR20IS, 2PR24IS

S/N 59-299-210-01. USE HAND CRIMPING TOOL MS10S-1					3PR18OS

WITH DIE S-6A AND SL-3A.

MS6SR			SIX PIN FEMALE CHASSIS MOUNT CONNECTOR,

MS-3120-10-6S,SLAC S/N59-299-410-51. USE

HAND CRIMP TOOL MS10S-1 WITH DIE

S-6A AND STOP SL-3A ONLY.

MS7P			SEVEN PIN CONNECTOR, MALE, MS-3106A-16S-1P,

AMPHENOL, SOLDER CONNECTIONS.

MS7S			SEVEN PIN CONNECTOR, FEMALE, MS-3106A-16S-1S,

AMPHENOL, SOLDER CONNECTIONS.

MS8P			EIGHT PIN CONNECTOR, MALE, MS-3126F-16-8P, SLAC			CONTROL, SSI	8C16/3V, 6PR22OS,

S/N 59-299-210-58. USE HAND CRIMPING TOOL M10S-1					8C18OS, 5C18TC

WITH DIE S-7 AND STOP SL-2 ONLY.

MS8PA			EIGHT PIN CONNECTOR, MALE, MS-3106E-22-23P, SOLDER					8C12T6V, 9C12T6V

CONNECTIONS.											4C12T6V, 4C10T6V

MS8PAR		EIGHT PIN CONNECTOR, MALE, MS-3102E-22-23P, MALE		FF BARREL		8C12T6V, 2C12TYR

RECEPTACLE, SOLDER CONNECTIONS.					QUAD TRIMS

MS8PW			EIGHT PIN CONNECTOR, MALE, MS-3106F-22-23PW, SOLDER					8C12T6V, 9C12T6V,

CONNECTIONS.											4C12T6V, 4C10T6V

MS8PY			EIGHT PIN CONNECTOR, MALE, MS-3106F-22-23PY, SOLDER					8C12T6V, 9C12T6V,

CONNECTIONS.											4C12T6V, 4C10T7V

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS8RPA		EIGHT PIN CONNECTOR, MALE RECEPTACLE. MS-3101E-22-23P.				2C12RR

AMPHENOL, SOLDER CONNECTIONS.

MS8S			EIGHT PIN CONNECTOR, FEMALE, MS-3126F-16-8S, SLAC		KLY, SSI		3C16/3V,5PR20OS,

S/N 59-299-210-08. USE HAND CRIMPING TOOL M10S-1					12C16/3V,

WITH DIE S-7 AND STOP SL-2 ONLY.								3PR22OS,8C16/3V

MS8SA			EIGHT PIN CONNECTOR, MS-3106E-22-23S, SOLDER						8C12T6V,9C12T6V,

CONNECTIONS.											4C12T6V,4C10T6V

MS8SB			EIGHT PIN CONNECTOR, FEMALE, MS3116F-14-5S.						9C18OS

NOT A STORES ITEM.

MS10P			TEN PIN CONNECTOR, MALE, MS-3126F-12-10P, SLAC						3PR22OS,2C16OS,

S/N59-299-210-53. USE HAND CRIMPING TOOL M10S-1 					10S22OS,20C20OS,

WITH DIE S-6A AND STOP SL-3A ONLY.								10C18OS,2C20OS,

10C16T3V

MS10PA		TEN PIN CONNECTOR, MALE, MS-3106A-18-19P, AMPHENOL,					4C20OS

SOLDER CONNECTIONS.

MS10PR		TEN PIN CONNECTOR, MALE CHASSIS RECEPTACLE,

MS3120F-12-10P, SLAC S/N59-299-410-03. USE HAND

CRIMPING TOOL M10S-1 WITH DIE S-6A AND STOP SL-3P ONLY.

MS10PRA           TEN PIN CONNECTOR, MALE RIGHT ANGLE PLUG, MS-3108R-18-IP.

ITT INDUSTRIES. SOLDER CONNECTION.

USED WITH BELDEN #83709 9C#16 CABLE AND

BELDEN #83715 15C#16 CABLE.

MS10S			TEN PIN CONNECTOR, FEMALE, MS-3126F-12-10S, SLAC		RF CAVITY		3PR22OS, 2C16OS,

S/N59-299-210-03. USE HAND CRIMPING TOOL M10S-1 		TUNER			2C20OS, 10C18OS

WITH DIE S-6A AND STOP SL-3A ONLY.

MS10SB		TEN PIN CONNECTOR, FEMALE, MS3106A-18-19S,						4PR22IS, 1PR22OS

AMPHENOL, SOLDER CONNECTIONS.

MS10SR		TEN PIN CONNECTOR, FEMALE RECEPTACLE,

MS3120-12-10S, SLAC S/N59-299-410-53. USE HAND

CRIMPING TOOL M10S-1 WITH DIE S-6A AND STOP SL-3A.

MS10SRA           TEN PIN CONNECTOR, FEMALE RIGHT ANGLE PLUG,

MS-3108R-18-IS.ITT INDUSTRIES. SOLDER CONNECTION.

USED WITH BELDEN #83709 9C#16 CABLE AND

BELDEN #83715 15C#16 CABLE.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS11P			ELEVEN PIN CONNECTOR, MS-3126F-18-11P,				SSI			12C16T6V

SLAC S/N59-299-210-60. USE HAND CRIMPING TOOL

M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS11PR		ELEVEN PIN CONNECTOR, MS-3120E-18-11P, MALE			FF BARREL		1PR16TS, 2C16/3V

RECEPTACLE, SLAC S/N59-299-410-10. USE HAND 			KLIXONS

CRIMPING TOOL M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS11PRA           ELEVEN PIN CONNECTOR, MALE RIGHT ANGLE PLUG,

MS-3108E-24-20P. AMPHENOL. SOLDER CONNECTION.

USED WITH BELDEN #83709 9C#16 CABLE AND

BELDEN #83715 15C#16 CABLE.

MS11S			ELEVEN PIN CONNECTOR, MS-3126F-18-11S, 				SSI, KICKER		5PR20OS, 12C16/3V,

SLAC S/N59-299-210-10. USE HAND CRIMPING 							5C16/6V

TOOL M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS11SRA           ELEVEN PIN CONNECTOR, FEMALE RIGHT ANGLE PLUG,

MS-3108E-24-20S. AMPHENOL. SOLDER CONNECTION.

USED WITH BELDEN #83709 9C#16 CABLE AND BELDEN

#83715 15C#16 CABLE.

MS12P			TWELVE PIN CONNECTOR, MALE PLUG, MS-3106A-24-12P,		MULTIBUS POWER

SOLDER CONNECTIONS.

MS12S			TWELVE PIN CONNECTOR, FEMALE PLUG, MS-3106A-24-12S,		MULTIBUS POWER

SOLDER CONNECTIONS.

MS12SA		TWELVE PIN CONNECTOR, FEMALE PLUG, ITT CANNON						6PR22IS

MS-3116F-14-12S, SOLDER CONNECTIONS.

MS13PV		THIRTEEN PIN CONNECTOR. INSERT: MOLDED SILICONE

RUBBER PER ZZ-R-765, CLASS 2B, GRADE 50, COLOR RED.

OPERATING VOLTAGE:5XVDC DIELECTRIC TESTING 7.5 KVDC

RATED. MFG CANTON P/N 3100A-CC18-13P.

MS13SV		THIRTEEN PIN CONNECTOR, SHELL: MS SIZE28

ALUMINUM PER MIL-C-5015. INSERT: MOLDED SILICONE

RUBBER PER ZZ-R-765, CLASS 2B, GRADE 70, COLOR RED.

MFG CANTON P/N 3106A-CC18-13S.

MS14P			FOURTEEN PIN CONNECTOR, MALE PLUG, ITT CANNON						3PR24IS

MS-3106F-20-27P, SOLDER CONNECTIONS.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS16P			SIXTEEN PIN CONNECTOR, MALE, MS-3126F-20-16P,			SEP PLATES/SSI	12C16T6V, 8PR16TS,

SLAC S/N59-299-210-62. USE HAND CRIMPING TOOL			KICKER/SSI		19C16/3V

M10S-1 WITH	DIE S-7 AND STOP SL-2 ONLY.

MS16PS		SIXTEEN PIN CONNECTOR, MALE, STRAIGHT PLUG,

SOLDER PINS, ITT-CANNON P/N MS3106A-24-5P.

MS16S			SIXTEEN PIN CONNECTOR, MS-3126F-20-16S,				VAR XFMR		19C16/3V

SLAC S/N59-299-210-12. USE HAND CRIMPING TOOL

M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS16SS		SIXTEEN PIN CONNECTOR, FEMALE, STRAIGHT PLUG,

SOLDER PINS, ITT-CANNON P/N MS3106A-24-5S.

MS19P			NINETEEN PIN CONNECTOR, MALE PLUG, MS-3126F-14-19P,		MPS			12PR22OS

SLAC S/N59-299-210-57. USE HAND CRIMP TOOL M10S-1

WITH DIE S7	AND STOP SL-3A ONLY.

MS19S			NINETEEN PIN CONNECTOR, FEMALE PLUG, MS-3126F-14-19S,		FLOW SW 		26C22/3C, 11PR22OS,

SLAC S/N59-299-210-07. USE HAND CRIMPING TOOL						18PR22OS, 8PR22OS

M10S-1 WITH	DIE S-6A AND STOP SL-3A ONLY.

MS19SA		NINETEEN PIN CONNECTOR, FEMALE PLUG, MS-3116F-14-19S.		SLMO			9PR18OS

MS20P			TWENTY PIN CONNECTOR, MALE PLUG, SOLDER CONNECTIONS,					19C18OS

ITT CANNON, MS3106-28-16P.

MS20S			TWENTY PIN CONNECTOR, FEMALE PLUG, SOLDER CONNECTIONS,

ITT CANNON, MS3106B-28-16S.

MS21P			TWENTY-ONE PIN CONNECTOR, MALE PLUG, MS-3126F-22-21P,					12C20J, 19C16T3V,

SLAC S/N59-299-210-65. USE HAND CRIMPING TOOL M10S-1 WITH				26C16T3V

DIE S-7 AND STOP SL-2 ONLY.

MS21S			TWENTY-ONE PIN CONNECTOR, FEMALE PLUG, MS-3126F-22-21S,				19C16T3V, 26C16T3V

SLAC S/N59-299-210-15. USE HAND CRIMPING TOOL M10S-1 WITH

DIE S-7 AND STOP SL-2 ONLY.

MS21SW		TWENTY-ONE PIN CONNECTOR, FEMALE PLUG, 				FF PROFILE		26C16T3V

MS-3126F-22-21SW, KEYED IN THE 'W' POSITION, 16 DEGREES 	MONITORS

OFF CENTER. NOT IN SLAC STORES, USE HAND CRIMPING TOOL

M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY. WIRE IN COLOR

CODE SEQUENCE. FOLD BACK THE UNUSED WIRES. SEE THE WIRE

TYPE FOR THE COLOR CODE.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS24PS		TWENTY-FOUR PIN CONNECTOR, MALE, STRAIGHT PLUG, SOLDER				12PR22SS

PINS, ITT-CANNON P/N MS3106A-24-28P.

MS24SS		TWENTY-FOUR PIN CONNECTOR, FEMALE, STRAIGHT PLUG,					12PR22SS

SOLDER PINS, ITT-CANNON P/N MS3106A-24-28S.

MS2411S		CONNECTORS, CIRCULAR, PLUG SOCKET, 97 SERIES,

9 CONTACTS, FEMALE 24 SHELL, ALUMINUM ALLOY BODY,

700 VDC/500 VRMS, SOLDER TERMINATION. NEWARK InOne

PART No: 91F8349, MANUFACTURER: AMPHENOL,

MANUFACTURER PART # 97-3106A-24-11S

MS26P			TWENTY-SIX PIN CONNECTOR, MALE PLUG, 				KICKER		26C16T3V

MS-3126F-16-26P SLAC S/N59-299-210-59. USE HAND

CRIMPING TOOL M10S-1 WITH DIE S-6A AND STOP SL-3A ONLY.

MS26PG		USE AN MS26P CONNECTOR, AND WIRE PER THE							15PR22OS

INSTRUCTIONS FOR THAT CONNECTOR. CONNECT A SHORT

LENGTH OF #20 AWG STRANDED GREEN (ONLY) WIRE TO

THE OVERALL SHIELD DRAIN WIRE, AND ATTACH THIS GREEN

WIRE TO THE SHELL OF THE CONNECTOR, USING AN LRR#6 LUG

UNDER ONE SCREW OF THE CABLE CLAMP.

MS26S			TWENTY-SIX PIN CONNECTOR, FEMALE PLUG, 				KICKER,LIMIT SW	26C16/3V, 13PR22OS,

MS-3126F-16-26S, SLAC S/N59-299-210-09. 							12C22T3V, 15PR22OS

USE HAND CRIMPING TOOL M10S-1 WITH

DIE S-6A AND STOP SL-3A ONLY.

MS26SA		TWENTY-SIX PIN CONNECTOR, FEMALE PLUG, SOLDER						12C18OS

CONNECTIONS. ITT-CANNON, P/N MS3106F-28-12S

MS27P			TWENTY-SEVEN PIN CONNECTOR, MALE PLUG, SOLDER PINS,

ITT-CANNON, P/N MS3106F-20-27P.

MS32P			THIRTY-TWO PIN CONNECTOR, MALE PLUG, 				KICKER/SSI		15PR22OS, 12PR22OS,

MS-3126F-18-32P, SLAC S/N 59-299-210-61. USE HAND					19C16T3V, 19PR24OS

CRIMPING TOOL M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS32S			THIRTY-TWO PIN CONNECTOR, FEMALE PLUG, 							19PR24OS,20C20OS

MS-3126F-18-32S, SLAC S/N59-299-210-11. USE HAND

CRIMPING TOOL M10S-1 WITH DIE S-7 AND STOP SL-2 ONLY.

MS41P			FORTY-ONE PIN CONNECTOR, MALE PLUG, MS-3126F-20-41P,		HEADSET,INTERCOM	19PR22IS

SLAC S/N59-299-210-64. USE HAND CRIMPING TOOL M10S-1

WITH DIE S-6A AND STOP SL-3A ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

MS41S			FORTY-ONE PIN CONNECTOR, FEMALE PLUG, MS-3126F-20-41S, 	HEADSET,INTERCOM	19PR22IS

USE HAND CRIMPING TOOL M10S-1 WITH DIES-6A AND

STOP SL-3A ONLY.

MTPFMMU		UNICAM MTP-COMPATIBLE, LASER-OPTIMIZED, 50 Um, MULTIMODE

CONNECTOR, 12-FIBER BLACK HOUSING AND AQUA BOOT, NO

(ALIGNMENT) PINS, (FEMALE). CORNING PART NUMBER 93-051-69-X

MTPFSMU		UNICAM MTP-COMPATIBLE, SINGLE-MODE CONNECTOR, 12-FIBER

GREEN HOUSING AND GREEN BOOT, NO (ALIGNMENT) PINS, (FEMALE).

CORNING PART NUMBER 93-201-69

N-PLIC		COAXIAL CONNECTOR, TYPE N PLUG TERMINATES ON ANDREWS					2.0HEL

HELIAX 1 5/8" HJ7-50A ANDREWS N-FEMALE P/N H7PNF NON

TUNABLE. BCS MPS PLIC.

NK-M8			EIGHT PIN CONNECTOR, MALE,AWG 8,PN:NK-M8-21C, STANDARD-K,

MFR:PEI-GENESIS.

N1/4HP		COAXIAL CONNECTOR, TYPE-N MALE, 1/4" FSJ1-50 HELIAX					1/4HEL,1/4HELS

CABLE PLUG ANDREW CAT. #41W, #41ASW, #C41SW, F1PNM-H.

N1/2HA		COAXIAL CONNECTOR, TYPE-N MALE 1/2" LDF4-50A						1/2HELA

CABLE PLUG ANDREW CAT. #L4PNM

N1/2HC		COAXIAL CONNECTOR, TYPE N, MALE, ANDREWS P/N F4PNMV2-HC,				1/2HELSF

50 OHM SYSTEM: LCLS RF SYSTEM

N1/2HD		COAXIAL CONNECTOR, TYPE-N, MALE, ANDREWS P/N 74AW,					1/2HELGF

MODIFIED ACCORDING TO DRWG SA-236-041-14.

N1/2HG		COAXIAL CONNECTOR, TYPE-N, FEMALE, ANDREWS P/N 74AN,					1/2HELGF

MODIFIED ACCORDING TO DRWG SA-236-041-14.

N1/2HJ		COAXIAL CONNECTOR, TYPE-N FEMALE JACK, 1/2" LDF4-50		RF SYSTEM		1/2HEL, 1/2HELS

HELIAX CABLE JACK. ANDREW CAT. #L44N. TERMINATE IN

ACCORDANCE WITH ANDREW BULLETIN 373838.

N1/2HP		COAXIAL CONNECTOR, TYPE-N MALE, 1/2" LDF4-50 OR			RF SYSTEM		1/2HEL, 1/2HELS

FSJ14-50B HELIAX CABLE PLUG. ANDREW CAT. #L44W 			FEEDBACK CAVITY

OR 44ASW. TERMINATE IN ACCORDANCE WITH

ANDREW BULLETIN 373838.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

N1/2MJ		COAXIAL CONNECTOR, TYPE-N FEMALE, 1/2" FSJ4-50B						1/2HELX4

HELIAX CABLE JACK, MODIFIED, ANDREW P/N 44ASN-15,

REXOLITE INSERT.

N1/2MR		COAXIAL CONNECTOR, TYPE-N MALE, 1/2" FSJ4-50B						1/2HELX4

HELIAX CABLE PLUG, ANDREW P/N 203540, REXOLITE INSERT.

N3/8HP		COAXIAL CONNECTOR, TYPE-N MALE, 3/8" LDF2-50 HELIAX					3/8HEL

CABLE PLUG. ANDREW CAT. #L42W, L2TNM-PL. TERMINATE IN

ACCORDANCE WITH ANDREW BULLETIN #7576087 REV. C.

N5/8HA		COAXIAL CONNECTOR, TYPE-N, FOR ANDREW LDF4.5-SERIES

5/8" ANNULAR-CORRUGATED HELIAX.  ANDREW PART

NUMBER: L4.5PNM-RC

N7/8GF		COAXIAL CONNECTOR, TYPE-N FEMALE JACK, 7/8" HJ5-50					7/8HELGF

HELIAX CABLE JACK. ANDREW CAT. #H5PNF. TERMINATE IN

ACCORDANCE WITH ANDREW BULLETIN 17925C.LION SYSTEM.

N7/8HJ		COAXIAL CONNECTOR, 7/8" LDF5-50 HELIAX CABLE			F SIG MLX,		7/8HEL

FEMALE JACK. ANDREW CAT. #L45N. TERMINATE IN			POS MONT,

ACCORDANCE WITH ANDREW BULLETIN 37374C.				WALL(I)MONT

N7/8HP		COAXIAL CONNECTOR, 7/8" LDF5-50 HELIAX CABLE MALE					7/8HEL

PLUG. ANDREW CAT. #L45W.

N8-A			COAXIAL CONNECTOR, TYPE N CABLE PLUG, ANDREW CAT.					RG58-A

#10804-101.USE TRIM CODE 402M.

N11			SAME CONNECTOR AS N213, BUT WIRE THE OUTER SHIELD OF 		DEC SYS		RG11TRI, RG11A

THE RG-11 TO A BANANA JACK. SEE DWG. IC15.

N58P			COAXIAL CONNECTOR TYPE N PLUG TERMINATES ON AN

RG58 OR RG141 COAXIAL CABLE. AMPHENOL P/N 82-5375.

USE CRIMPING TOOL CTL-3. USE DIE SET 227-1221-57.

N200			COAXIAL CONNECTOR, TYPE "N" MALE PLUG, TIMES			BPMS			LMR200,LMR200FR

MICROWAVE SYSTEMS CAT. #TC-200-NM OR EQUIVALENT.

N200BJ		COAXIAL CONNECTOR, TYPE N FEMALE BULK-HEAD JACK. 		BPMS			LMR200, LMR200FR

CONNEX #172217. RF CONNECTORS RFN-1022-8-C2 OR

EQUIVALENT.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

N213			COAXIAL CONNECTOR, TYPE N CABLE PLUG. KINGS CAT. NO. 		KICKER, GENERAL	R11TRI, RG213

KN-59-67, KN-59-132 OR KN-59-202, 					PURPOSE TRUNK.	RG8

SLAC S/N59-299-018-52. USE KINGS CRIMPING TOOL KTH-1000

WITH DIE KTH-2003 AND TRIM CODE 402M FOR KN-59-67 AND

KN-59-132, AND DIE KTH-2004 AND TRIM CODE 480

FOR KN-59-202.

N213MC		COAXIAL CONNECTOR, TYPE N CABLE PLUG. KINGS CAT. NO. 		INJ. KICKER		RG8

KN-59-19, MODIFIED TO SPECIFICATIONS AS SHOWN ON		MODULATOR

DRAWING #CA-344-296-01 CONNECTOR TERMINATES AN

RG8 COAXIAL CABLE. USE KINGS CRIMPING TOOL KTH-1000

WITH DIE KTH-2003. SEE DRAWING #CA-344-296-01

FOR CABLE TRIM CODE.

N214			COAXIAL CONNECTOR, TYPE N CABLE PLUG. KINGS CAT. NO.		OPTL MONT		RG214

KN-59-68, KN-59-104 OR KN-59-105, SLAC S/N59-299-018-53.

USE KINGS CRIMPING TOOL KTH-1000 WITH DIE KTH-2004 AND

TRIM CODE 402.

N214M			COAXIAL CONNECTOR, TYPE N CABLE PLUG. KINGS CAT. 		ABORT KICKER	RG8

NO.KN-59-489, MODIFIED TO SPECIFICATIONS AS SHOWN		MODULATOR

ON DRAWING #CA-344-293-00. CONNECTOR TERMINATES

AN RG8 COAXIAL CABLE. SEE DRAWING #CA-344-293-00

FOR CABLE TRIM CODE AND TERMINATION SPECIFICATION.

N214-F		COAXIAL CONNECTOR, TYPE N CABLE JACK, KINGS 						RG214

CAT-# KN39-83,SLAC P/N 59-299-018-60. USE KINGS

CRIMPING TOOL KHT-1000 WITHDIE KTH-2004 AND TRIM

CODE 402M.

N214JB		COAX CONNECTOR, TYPE N CABLE JACK, BULKHEAD, 						RG214

KINGS 19-87,SLAC P/N59-299-018-64. USE KINGS

CRIMPING TOOL KTH-1000 WITH DIE KTH-2004 AND TRIM

CODE 402M.

N218			COAXIAL CONNECTOR, TYPE N CABLE PLUG, UG-167A/U,					RG218R

KINGS P/N KN-59-214.

N223			COAXIAL CONNECTOR, TYPE N CABLE PLUG, KINGS K-GRIP JR,	FF BPM’S		RG223,RG223X4

KINGS CAT-# KN-59-160, USE KINGS CRIMPING TOOL KTH-2061,

JACKET TRIM JIG KTJ-108 AND DIELECTRIC TRIM JIG KTD-38.

N240			COAXIAL CONNECTOR, TYPE N MALE PLUG					BPMS			LMR240,LMR240FR

TIMES MICROWAVE SYSTEMS CAT#TC-240-NMH

OR EQUIVALENT.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

N240BJ		COAXIAL CONNECTOR, TYPE N FEMALE BULK-				BPMS,			LMR240, LMR240FR

HEAD JACK. TIMES MICROWAVE SYSTEMS CAT.				SRRL HIGH

#TC-240-NF-BHF, AMPHENOL #172149 OR EQUIVALENT.			QUALITY

N400			COAXIAL CONNECTOR, TYPE N MALE PLUG					BPMS			LMR400,LMR400FR

TIMES MICROWAVE SYSTEMS CAT. #TC-400-NMH,

EZ-400-NMH OR EQUIVALENT.

N400BJ		COAXIAL CONNECTOR, TYPE N FEMALE BULK-				BPMS			LMR400,LMR400FR

HEAD JACK. TIMES MICROWAVE SYSTEMS CAT.

#TC-400-NFBC-PE, EZ-400-NF-BH OR EQUIVALENT.

N-50UV		COAXIAL CONNECTOR, TYPE N CABLE PLUG WATER PROTECTION 				WPMCOAX

ACCORDING TO IP67,UV PROTECTION, 50ohm, HUBER+SUHNER

Man P/N 11 N-50-10-5/103 UV USED FOR THE WPM RF SIGNAL

N600			COAXIAL CONNECTOR, TYPE N MALE PLUG					BPMS			LMR600,LMR600FR

TIMES MICROWAVE SYSTEMS CAT. # EZ-600-NMH-D

OR EQUIVALENT.

N600BJ		COAXIAL CONNECTOR, TYPE N FEMALE BULK-				BPMS			LMR600,LMR600FR

HEAD JACK. TIMES MICROWAVE SYSTEMS CAT.

#EZ-600-NF-BH OR EQUIVALENT.

OPAL-Y		SLAC MADE POWER CABLE TO FEED AN OPAL 1000

CAMERA AND A EDT RCX CAMERALINK TO FIBER CONVERTER.

DETAILS FOR THE OPAL-Y CONNECTIONS ARE SHOWN IN

DRAWING CA-261-801-31 .

OPTIC			THIS CONNECTOR IS AN OVERALL NAME OF THE CONNECTOR		SLD POLARIMETER	FIBOPT1

THAT THE FACTORY INSTALLS ON A FIBER OPTIC CABLE. THIS	FIBER OPTICS

CONNECTOR IS TO BE INSTALLED BY QUALIFIED PERSONNEL ONLY.

PC10TB-F		TEN PIN FEMALE CONNECTOR, SILVER PLATED PINS			MAG_PROBES

WITH DIAMETER OF 1MM LOCATED INSIDE OF CERAMIC

ISOLATOR. MFG: RUSKIE.

PC10TB-M		TEN PIN MALE RECEPTACLE, SILVER PLATED PINS			MAG_PROBES

WITH DIAMETER OF 1MM LOCATED INSIDE OF CERAMIC

ISOLATOR. MFG: RUSKIE.

PC32TB-F		THIRTY TWO PIN FEMALE CONNECTOR, SILVER PLATED PINS		MAG_PROBES

WITH DIAMETER OF 1MM LOCATED INSIDE OF CERAMIC

ISOLATOR. MFG: RUSKIE.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PC32TB-M		THIRTY TWO PIN MALE RECEPTACLE, SILVER PLATED PINS		MAG_PROBES

WITH DIAMETER OF 1MM LOCATED INSIDE OF CERAMIC

ISOLATOR. MFG: RUSKIE.

PHONE			PHONE PLUG, 3/32" DIAMETER, 2 CONTACTS, RADIO SHACK

ARCHER P/N 274-279.

PHON-R		RIGHT ANGLE PHONE PLUG, 1/4" DIAMETER, TWO

CONTACTS, TYPE NP2RC-BAG, NEWARK CAT. #89F6034.

PHXQP1		ONE POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER.

SEE PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED

ASSEMBLY/TERMINATION DRAWING NUMBER. DO NOT STRIP

CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK

FULLY FLUSH WITH CONNECTOR BODY AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE:QP 1.5/1(BU OR GN/YE)

ORDER NUMBER: 3051108, (3051250, or 3051263).

**DO NOT USE TEFLON WIRE **

PHXQP2	TWO POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER.

SEE PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED

ASSEMBLY/TERMINATION DRAWING NUMBER.DO NOT STRIP

CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK

FULLY FLUSH WITH CONNECTOR BODY AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE: QP 1.5/2

ORDER NUMBER: 3051111. SEE “SELF-ASSEMBLED COMBI PLUGS

WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT “CLIPLINE”

CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PHXQP3	THREE POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER.

SEE PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED

ASSEMBLY/TERMINATION DRAWING NUMBER. DO NOT STRIP

CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK

FULLY FLUSH WITH CONNECTOR BODY AND LOCK CONDUCTOR IN

PLACE.MANUFACTURER: PHOENIX CONTACT. TYPE: QP 1.5/3

ORDER NUMBER: 3051124. SEE “SELF-ASSEMBLED COMBI PLUGS

WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT

“CLIPLINE” CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXQP4	FOUR POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM LEFT

AT 1 WITH COMBI CONNECTOR KEYS FACING USER. SEE PIN

LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED ASSEMBLY/

TERMINATION DRAWING NUMBER. DO NOT STRIP CONDUCTOR.

3/4-INCH INSERTION LENGTH. USE SCREWDRIVER IN RECTANGULAR

HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK FULLY FLUSH WITH

CONNECTOR BODY AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE: QP 1.5/4

ORDER NUMBER: 3051137. SEE “SELF-ASSEMBLED COMBI PLUGS

WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT “CLIPLINE”

CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXQP5	FIVE POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM LEFT AT 1

WITH COMBI CONNECTOR KEYS FACING USER. SEE PIN LIST FOR

CONDUCTOR ASSIGNMENT OR DETAILED ASSEMBLY/TERMINATION

DRAWING NUMBER. DO NOT STRIP CONDUCTOR. 3/4-INCH INSERTION

LENGTH. USE SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE

WIRE ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT.

TYPE: QP 1.5/5 ORDER NUMBER: 3051140. SEE “SELF-ASSEMBLED

COMBI PLUGS WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT

“CLIPLINE” CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PHXQP6	SIX POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER.

SEE PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED

ASSEMBLY/TERMINATION DRAWING NUMBER. DO NOT STRIP

CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK

FULLY FLUSH WITH CONNECTOR BODY AND LOCK CONDUCTOR IN

PLACE. MANUFACTURER: PHOENIX CONTACT. TYPE: QP 1.5/6

ORDER NUMBER: 3051153. SEE “SELF-ASSEMBLED COMBI PLUGS

WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT

“CLIPLINE” CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXQP7	SEVEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM LEFT

AT 1 WITH COMBI CONNECTOR KEYS FACING USER. SEE PIN

LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED ASSEMBLY/TERMINATION

DRAWING NUMBER. DO NOT STRIP CONDUCTOR. 3/4-INCH INSERTION

LENGTH. USE SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE

ORANGE WIRE ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT.

TYPE: QP 1.5/7 ORDER NUMBER: 3051166. SEE “SELF-ASSEMBLED

COMBI PLUGS WITH FAST CONNECTION” SECTION OF PHOENIX CONTACT

“CLIPLINE” CATALOG FOR ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXQP8	EIGHT POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM LEFT

AT 1 WITH COMBI CONNECTOR KEYS FACING USER. SEE PIN

LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED ASSEMBLY/

TERMINATION DRAWING NUMBER. DO NOT STRIP CONDUCTOR.

3/4-INCH INSERTION LENGTH. USE SCREWDRIVER IN RECTANGULAR

HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK FULLY FLUSH WITH

CONNECTOR BODY AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE: QP 1.5/8 ORDER NUMBER:

3051179. SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR ADDITIONAL

CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PHXQP9	NINE POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING

STARTS FROM LEFT AT 1 WITH COMBI CONNECTOR KEYS

FACING USER. SEE PIN LIST FOR CONDUCTOR ASSIGNMENT

OR DETAILED ASSEMBLY/TERMINATION DRAWING NUMBER. DO

NOT STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE

SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE

ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT.

TYPE: QP 1.5/9 ORDER NUMBER: 3051182. SEE “SELF-ASSEMBLED

COMBI PLUGS WITH FAST CONNECTION” SECTION OF PHOENIX

CONTACT “CLIPLINE” CATALOG FOR ADDITIONAL

CONFIGURATION OPTIONS.**DO NOT USE TEFLON WIRE **

PHXQP10	TEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING  STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER. SEE

PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED ASSEMBLY/

TERMINATION DRAWING NUMBER. DO NOT STRIP CONDUCTOR. 3/4-INCH

INSERTION LENGTH. USE SCREWDRIVER IN RECTANGULAR HOLE TO

ROTATE ORANGE WIRE ENTRY BLOCK FULLY FLUSH WITH CONNECTOR

BODY AND LOCK CONDUCTOR IN PLACE. MANUFACTURER:

PHOENIX CONTACT.TYPE: QP 1.5/10 ORDER NUMBER: 3051195.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXQP11		ELEVEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING

STARTS FROM LEFT AT 1 WITH COMBI CONNECTOR KEYS

FACING USER. SEE PIN LIST FOR CONDUCTOR ASSIGNMENT

OR DETAILED ASSEMBLY/TERMINATION DRAWING NUMBER. DO

NOT STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE

SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE

ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT

TYPE: QP 1.5/11 ORDER NUMBER: 3051205.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PHXQP12		TWELVE POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING STARTS FROM

LEFT AT 1 WITH COMBI CONNECTOR KEYS FACING USER.

SEE PIN LIST FOR CONDUCTOR ASSIGNMENT OR DETAILED

ASSEMBLY/TERMINATION DRAWING NUMBER. DO NOT STRIP

CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY

BLOCK FULLY FLUSH WITH CONNECTOR BODY AND LOCK

CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT

TYPE: QP 1.5/12 ORDER NUMBER: 3051218.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.**DO NOT USE TEFLON WIRE **

PHXQP13		THIRTEEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING

STARTS FROM LEFT AT 1 WITH COMBI CONNECTOR KEYS

FACING USER. SEE PIN LIST FOR CONDUCTOR ASSIGNMENT

OR DETAILED ASSEMBLY/TERMINATION DRAWING NUMBER. DO

NOT STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE

SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE

ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT

TYPE: QP 1.5/13 ORDER NUMBER: 3051221.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.**DO NOT USE TEFLON WIRE **

PHXQP14		FOURTEEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING

STARTS FROM LEFT AT 1 WITH COMBI CONNECTOR KEYS

FACING USER. SEE PIN LIST FOR CONDUCTOR ASSIGNMENT

OR DETAILED ASSEMBLY/TERMINATION DRAWING NUMBER. DO

NOT STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE

SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE

ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT

TYPE: QP 1.5/14 ORDER NUMBER: 3051234.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PHXQP15		FIFTEEN POSITION CONNECTOR, "COMBI" TYPE PLUG,

"QUICKCON" INSULATION DISPLACEMENT TERMINATION.

WIRE RANGE: 24-16 AWG. PIN NUMBERING

STARTS FROM LEFT AT 1 WITH COMBI CONNECTOR KEYS

FACING USER. SEE PIN LIST FOR CONDUCTOR ASSIGNMENT

OR DETAILED ASSEMBLY/TERMINATION DRAWING NUMBER. DO

NOT STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE

SCREWDRIVER IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE

ENTRY BLOCK FULLY FLUSH WITH CONNECTOR BODY AND

LOCK CONDUCTOR IN PLACE. MANUFACTURER: PHOENIX CONTACT

TYPE: QP 1.5/15 ORDER NUMBER: 3051247.

SEE “SELF-ASSEMBLED COMBI PLUGS WITH FAST CONNECTION”

SECTION OF PHOENIX CONTACT “CLIPLINE” CATALOG FOR

ADDITIONAL CONFIGURATION OPTIONS.

**DO NOT USE TEFLON WIRE **

PHXTB2		   TWO POSITION TERMINAL BUS, DIN RAIL MOUNT,

10MM BOLT DIAMETER RING LUG TERMINATION,

WIRE SIZE: 6 AWG TO 1/0 AWG.

PHOENIX CONTACT TYPE: UHV 50-AS/AS, P/N:2130017 .

P15QTC		ONE POSITION TERMINAL BLOCK, DIN RAIL MOUNT, WIRE RANGE:

24-16AWG,(QTC 1,5), TERMINATE CONDUCTOR TO SPECIFIED"QUICKCON"

INSULATION DISPLACEMENT CONNECTOR ON TERMINAL BLOCK. DO NOT

STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK FULLY

FLUSH WITH TERMINAL BLOCK AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE: QTC 1,5(BU OR -PE)

ORDER NUMBER: 3205019, (3205022, OR 3205035).

SEE PHOENIX CONTACT "CLIPLINE" CATALOG FOR ADDITIONAL

TERMINAL BLOCK OPTIONS THAT INCLUDE "QUICKCON" INSULATION

DISPLACEMENT CONNECTION.

**DO NOT USE TEFLON WIRE **

P25QTC		ONE POSITION TERMINAL BLOCK, DIN RAIL MOUNT, WIRE RANGE:

20-14AWG,(QTC 2,5), TERMINATE CONDUCTOR TO SPECIFIED"QUICKCON"

INSULATION DISPLACEMENT CONNECTOR ON TERMINAL BLOCK. DO NOT

STRIP CONDUCTOR. 3/4-INCH INSERTION LENGTH. USE SCREWDRIVER

IN RECTANGULAR HOLE TO ROTATE ORANGE WIRE ENTRY BLOCK FULLY

FLUSH WITH TERMINAL BLOCK AND LOCK CONDUCTOR IN PLACE.

MANUFACTURER: PHOENIX CONTACT. TYPE: QTC 2,5(BU OR -PE)

ORDER NUMBER: 3209416, (3206429, OR 3206432).

SEE PHOENIX CONTACT "CLIPLINE" CATALOG FOR ADDITIONAL

TERMINAL BLOCK OPTIONS THAT INCLUDE "QUICKCON" INSULATION

DISPLACEMENT CONNECTION.**DO NOT USE TEFLON WIRE **

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PLB06P		6 PIN, 2 ROW, MALE CONNECTOR, TOP OPENING HOOD.

POSITRONIC INDUSTRIES, CODE NUMBER PLB06M0050.

PLB06S		6 PIN, 2 ROW, FEMALE CONNECTOR, TOP OPENING HOOD.

POSITRONIC INDUSTRIES, CODE NUMBER PLB06F0050.

PLC30P		30 PIN, 3 ROW, MALE CONNECTOR, TOP OPENING HOOD.

POSITRONIC INDUSTRIES, CODE NUMBER PLC30M0050.

PLC30S		30 PIN, 3 ROW, FEMALE CONNECTOR, TOP OPENING HOOD.

POSITRONIC INDUSTRIES, CODE NUMBER PLC30F0050.

POS19PS		CONNECTOR, POSITRONIX FRONT RUNNER SERIES,SIZE 19

HOUSING, FREE IN LINE MALE CONTACTS W/PLUGHOUSING,

19 PINS-SIZE 20, EMI/RFI SHIELDED SERVICE CLASS,

SHORT-STRAIGHT EMI/RFI CABLE ADAPTOR HOOD.

POSITRONIX PART NUMBER - FR19MP1920M6.(USES SIZE 20

REMOVABLE MALE (PIN) CONTACTS P/N MC720N3)

POS19RS		CONNECTOR, POSITRONIC FRONT RUNNER SERIES,SIZE 19

HOUSING, FREE IN LINE FEMALE CONTACTS W/PLUGHOUSING,

19 PINS-SIZE 20, EMI/RFI SHIELDED SERVICE CLASS,

SHORT-STRAIGHT EMI/RFI CABLE ADAPTOR HOOD.

POSITRONIC PART NUMBER - FR19FP1920M6(USES SIZE 20

REMOVABLE FEMALE (PIN) CONTACTS P/N FC720N2)

PP50G			CONNECTOR, MALE, 50 A, 125-250 VOLT AC OR DC CURRENT

RUPTURING. SUPERIOR ELECTRIC CAT-# PP50GB.

PP75-B		ANDERSON POWERPOLE 75 AMP LOCKING CONNECTOR,PP75

LOCKING HOUSING 75LOKBLK "BLACK" MCORS, TSP, QMS.

PP75-R		ANDERSON POWERPOLE 75 AMP LOCKING CONNECTOR,PP75

LOCKING HOUSING 75LOKRED "RED" MCORS, TSP, QMS.

PP100G		CONNECTOR, MALE, 100A, 125-250 VOLTS AC OR DC CURRENT					#1-AL

RUPTURING. SUPERIOR ELECTRIC CAT-# PP100GB.

PP180A		CONNECTOR PLUG, MALE, 18AMP P/N 1381G1 (BLACK), 		MCOR			#2

1381G2 (WHITE). USEP/N 1383 CONTACT FOR #2 AWG.

PP180-B		ANDERSON POWERPOLE 180AMP CONNECTOR, PP180 SERIES		MCOR

HOUSING 1381G1 "BLACK"

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

PP180C		ANDERSON POWERPOLE 180AMP CONTACT, 1/0 WIRE SIZE		MCOR			#1/0-FLEX

USE WITH PP180 SERIES HOUSING, ANDERSON POWER P/N 1382.

PP180-R		ANDERSON POWERPOLE 180AMP CONNECTOR, PP180 SERIES 		MCOR

HOUSING 1381G3 "RED"

PPR8			8 POLE RECEPTACLE, ANDERSON POWERPOLE CAT. #1454G1		MCOR DC OUT		2C12OS

POWERPOLE PAK RECEPTACLE.

PREFAB		CABLE AND CONNECTOR DETAILS ARE PROVIDED BY

OUTSIDE VENDOR.

PS50/2		CONNECTORS RS50G & PP50G ARE USED. WIRE AS FOLLOWS:

RS50G TO "R" & PP50G TO "G".

PT8S			8 PIN CONNECTOR, FEMALE, BENDIX P/N PT06A-X-8S			SLMO			4PR22OS

PUSHON		THIS INDICATES A CONNECTION WHERE THE WIRE IS						19PR22IS

PUSHED ONTO THE TERMINATION POINT AS PART OF THE FIELD

INSTALLATION OF A CABLE.

RG58C/U		COAXIAL CONNECTOR, SLEEVE, CONTACT, F/COAXIAL,

KINGS K-GRIP (FERRULE), PART No. 1205-19-5

FOR CRIMPING USE DIE SIZE 42. SLAC S/N 59-299-009-01.

RG-6QS		CONTROLNET BNC PLUG RG-6QS USE 1786-CTK TOOLKIT 		CONTROLNET		RG6-QF

WITH 2082 DIE SET AND CRIMP SETTING OF 4 ALLEN BRADLEY

PN# 1786-BNC/B.

RJ12			SIX PIN CONNECTOR WITH ONE PIECE CONSTRUCTION AND

PRELOADED CONTACTS. RATED 150V @1.5 MAX.

AMP P/N# 5.5551777-3 OR EQUIVALENT.

RJ45			EIGHT PIN CONNECTOR WITH ONE PIECE CONSTRUCTION AND

PRELOADED CONTACTS. RATED 250 VAC@2A MAX. TENSILE

STRENGTH (CABLE TO PLUG) 20 LBS. AMP P/N#5.641339-3

OR EQIVALENT.

RS50G			CONNECTOR, FEMALE, 50A, 125-250 VOLT AC OR DC CURRENT

RUPTURING. SUPERIOR ELECTRIC CAT-# RS50GWT.

RS100G		CONNECTOR, FEMALE, 100A, 125-250 VOLTS AC OR DC CURRENT				#1-AL

RUPTURING. SUPERIOR ELECTRIC CAT-# RS100GWT.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

RTDS			SPECIAL THREE PIN FEMALE CONNECTOR, WHITE SHELL. MATES				2PR24IS

WITH RTD-MOUNTED PLUG. OMEGA P/N OPT-U-F.

S1/2RP		COAXIAL CONNECTOR FOR 1/2" SEMI-RIGID JT-4500 SERIES		CATV SYSTEM		1/2”RD, 1/2"RDB

COAXIAL CABLE. GILBERT PART NO. GRS-500-CH-DU-03. SEE

THE GILBERT CATALOG FOR TRIM AND ASSEMBLY INSTRUCTIONS.

S3/4RP		COAXIAL CONNECTOR FOR 3/4" SEMI-RIGID JT-4750 SERIES		CATV SYSTEM		3/4”RGD

COAXIAL CABLE. GILBERT PART NO. GRS-750-CH-DU-01.SEE THE

GILBERT CATALOG FOR TRIM AND ASSEMBLY INSTRUCTIONS.

SC			FIBER OPTIC CONNECTOR. TYPE 'SC' UNICAM CONNECTOR,

CERAMIC TIP,ROTATING CAM; INSERTION LOSS: 0.3Db TYPICAL;

NOMINAL FIBER O.D.:125um; MFG SIECOR,

MULTIMODE P/N 95-000-41, SINGLEMODE P/N 95-200-41.

SC760		   SWITCHCRAFT LOW VOLTAGE POWER CONNECTOR. CONNECTOR IS

FEMALE TYPE WITH A 2.1 MM CENTER HOLE AND BLACK SHIELD.

DISTRIBUTOR ALLIED INDUSTRIES

POWER PLUG MFR. PART#: 760 ALLIED STOCK#: 932-0760

SCS760		SWITCHCRAFT LOW VOLTAGE POWER CONNECTOR. CONNECTOR IS

FEMALE TYPE WITH A 1.6 MM CENTER HOLE AND BLACK SHIELD.

DISTRIBUTOR ALLIED INDUSTRIES

POWER PLUG MFR. PART#: S760 ALLIED STOCK#: 932-9999

SCSI-2		FIFTY PIN CONNECTOR. SHIELDED PLUG WITH ASSEMBLED

STANDARD TERMINATION COVERS. AMPLIMITE SERIES III

THERMOPLASTIC, MFG AMP P/N 749111-4.

SHV-C		   COAXIAL CONNECTOR, 5KV, SHV CABLE PLUG, KINGS NO.				    TYPE-C

1705-16-M06, SLAC S/N 59-299-035-16 FOR

THE STANDARD TYPE INSULATION MATERIAL. KINGS NO.

1705-16-11, SLAC S/N 59-299-035-15 FOR

THE REXOLITE INSULATION TYPE. USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE KTH-2061 AND TRIM CODE 441.

SHV-10K		COAXIAL PLUG CONNECTOR FOR DC CONNECTIONS ONLY. RATED UP TO

10KV OF DC, TYPICAL PART: KINGS ELECTRONICS: 1065-2.

http://www.kingselectronics.com/Portals/0/SalesPDF/1065-2_SD.pdf

SHVMOD		SLAC BUILT HV CONNECTOR. USED ON 1/4" HELB						1/4" HELB

HELIAX CABLE. USED BY CONTROLS DEPARTMENT.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

SHV58			COAXIAL CONNECTOR, SHV CABLE PLUG, 5KV. KINGS NO. 		FAST SENSOR		RG58R

1705-2,SLAC S/N59-299-035-11. USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE KTH-2061 AND TRIM CODE 441.

SHV59J		COAXIAL CONNECTOR, 5KV, SHV BULKHEAD JACK. KINGS NO.					RG59R

1702-1, SLAC S/N59-299-035-68. USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE KTH-2062 AND TRIM CODE 441.

SHV59			COAXIAL CONNECTOR, 5KV, SHV CABLE PLUG. KINGS NO. 					RG59R

1705-1,SLAC S/N 59-299-035-12. USE KINGS CRIMPING

TOOL KTH-1000 WITH DIE KTH-2062 AND TRIM CODE 418.

SHV214		COAXIAL CONNECTOR 5KV, SHV CABLE PLUG, KINGS

CAT#1705-4,	SLAC S/N59-299-035-14. USE KING CRIMPING TOOL

KTH-1000 WITH DIE KTH-1079 AND TRIM CODE 457.

SL1808B		EIGHT PIN CONNECTOR, PC BOARD TO CABLE, TWO PIECE SNAP

LOCK DESIGN. SOLDERS TO PC BOARD. CABLE END TERMINATES

TO CONNECTOR WITH INTEGRATED SET SCREWS.

WEIDMULLER CAT#123676. USED FOR REVERSING SWITCH CONTROLLER.

SLAC7			SLAC BUILT SEVEN PIN CONNECTOR. USED TO MONITOR THE					4PR22OS

POWER SUPPLIES IN A NIM CRATE. USED BY SLAC CONTROLS DEPT.

SMA			SMA MALE STRAIGHT PLUG, TIMES MICROWAVE SYSTEMS,

LOW LOSS LOW PASSIVE INTERMOD COAX PART NUMBER # TC-400-SM				LMR400FR

SMA1/4H		SMA MALE FOR 1/4 IN FSJ1-50A CABLE, INTERFACE SMA MALE,

BODY STYLE STRAIGHT, BRAND HELIAX, MOUNTING ANGLE STRAIGHT,

CONNECTOR IMPEDANCE 50 OHM, OPERATING FREQUENCY BAND 0 - 18000 MHZ.

CABLE IMPEDANCE 50 OHM, RF OPERATING VOLTAGE, MAX (VRMS)500.00V

DC TEST VOLTAGE 1000V, OUTER CONTACT RESISTANCE, MAX 2.50 MOHM,

INNER CONTACT RESISTANCE, MINIMUM 5000 MOHM, AVERAGE POWER 0.4KW @ 900MHZ,

PEAK POWER, MAX 5.00KW, SHIELDING EFFECTIVENESS -110 DB.

PART#  F1TSM-HF.

SMA3/8H		COAXIAL CONNECTOR, TYPE SMA, MALE. ANDREWS P/N E2TSM,					EFX2RN-50

SMA STRAIGHT MALE CONNECTOR FOR EFX2-50, LDF2-50 SYSTEM:				LDF2-50(3/8HELSF)

LCLS RF SYSTEM.

SMA58			COAXIAL CONNECTOR, SMA STRAIGHT CABLE PLUG. SEALECTRO		FFTB VAC		RG58

NO. 50-624-9141-31 OR OMNI/SPECTRA P/N 2036-5014-00,

MOD. #636-2A.

SMA214		TERMINATE CABLE USING AN N214-F CONNECTOR, THEN			SPECIAL BPM		EG214

INSTALL AN SMA/N ADAPTER.						CABLES

SMA223		COAXIAL CONNECTOR, SMA STRAIGHT CABLE PLUG.			BEAM POSITION	RG223X4

SELECTRO NO. 50-622-9142-31 OR CABLEWAVE NO.545-001		MONITORS

OR SOLITRON NO. 2900-6001, KINGS NO. 875-5-3, USE

CRIMPING DIE SET KTH-2001, JACKET TRIM JIG KTJ-78,

DIELECTRIC TRIM JIG KTD-116, TRIM CODE 432.

SLAC S/N59-299-040-01.

SMA240		TYPE SMA MALE PLUG CONNECTOR FOR LMR-240 STAINLESS 					LMR240

STEEL W/ GOLD PLATED BERYLLIUM COPPER 50 OHMS 1000

VOLTS(RMS MAX)1.25:1 UP TO 2 GHz.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

SMA/N			ADAPTER, SMA FEMALE TO N FEMALE, PANEL MOUNT (BULKHEAD	SLC FF BPM'S	RG223, RG214

ADAPTER), PASTERNAK ENTERPRISES CAT-# PE-9104.

SMR223		COAXIAL CONNECTOR, SMA RIGHT ANGLE CABLE PLUG.			BEAM POSITION	RG223,RG223X4

SELECTRO NO.50-628-9142-30 OR CABLEWAVE NO. 555-001 OR	MONITORS

SOLITRON NO. 2910-6001, KINGS NO. 876-11-3, USE

CRIMPING DIE SET KTH-2001, JACKET TRIM JIG KTJ-78,

DIELECTRIC TRIM JIG KTD-116, TRIM CODE 432.

NOT IN STORES.

SMS9P			NINE PIN CONNECTOR, MALE, BURNDY P/N SMS-9P-1

SMS12P		TWELVE PIN CONNECTOR, MALE, BURNDY P/N SMS-12P-1

SOLDER		THIS INDICATES A CONNECTION WHERE THE INDICATED						27PR22OS, 1PR20OS,

WIRE IS SOLDERED DIRECTLY TO THE INDICATED 						12PR22SS

TERMINATION	POINT, AS PART OF THE FIELD INSTALLATION

OF THE INDICATED CABLE.

SP1/2H		COAXIAL SPLICE FOR 1/2" LDF4-50 HELIAX CABLE. ANDREW		CABLE SPLICES	1/2HEL,1/2HELS

CAT. NO. L44Z. CONNECT IN ACCORDANCE WITH ANDREW

BULLETIN 37384.

SP7/8H		COAXIAL SPLICE FOR 7/8" LDF5-50 HELIAX CABLE. ANDREW		CABLE SPLICES	7/8HEL

CAT. NO. L45Z. CONNECT IN ACCORDANCE WITH ANDREW

BULLETIN 37381.

SPEC			THIS TYPE OF TERMINATION IS USED ONLY FOR SPECIAL PULSED

COAXIAL CABLE CONNECTIONS, SUCH AS KICKER HIGH VOLTAGE

CONNECTIONS. ONLY SYSTEM SPECIALISTS ARE TO TERMINATE

AND MAKE CONNECTIONS.

S&T			THIS INDICATES A WIRE IS STRIPPED AND TINNED AND

CONNECTED TO THE DESIGNATED POINTS.

ST			FIBER OPTIC CONNECTOR. TYPE 'ST' UNICAM CONNECTOR,

CERAMIC TIP, ROTATING CAM; INSERTION LOSS: 0.3Db TYPICAL;

NOMINAL FIBER O.D.:125um; MFG SIECOR,

MULTIMODE P/N 95-000-51, SINGLEMODE P/N 95-200-51.

STARCEL		SPECIAL CONNECTOR, HIGH VOLTAGE FOR VARIAN ION PUMP. 					TYPE-C

MFG: GAMMA VACUUM, ADDRESS: 2915 133RD STREET WEST,

SHAKOPEE, MN 55379.  MFG P/N 380101

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

STRIP			THIS INDICATES A CONNECTION WHERE THE INDICATED WIRE 					250MCM, 350MCM,

IS STRIPPED TO THE PROPER LENGTH, INSERTED INTO THE 					500MCM,#4/0,

TERMINAL AND THE SCREW TIGHTENED TO MANUFACTURE SPECIFIED 				#6-,#8-,

TORQUE, AS PART OF THE FIELD INSTALLATION OF THE INDICATED				#10-,#12-,

CABLE,ALUMINUM WIRES MUST BE INSTALLED USING AN OXIDE 				2C14TYR, THRM-CU

INHIBITING ELECTRICAL JOINT COMPOUND (SEE GENERAL NOTE #8

AT THE BEGINNING OF THIS DOCUMENT).

STRP-A		STRIP 3/8 OF AN INCH OF INSULATION FROM THE ENDS OF

THE PAIR WIRES. USING THE WIRE COLOR-CODE FROM TABLE 1,

CONNECT THE FIRST WIRE OF THE PAIR TO THE '+' POINT,

THE SECOND WIRE TO THE '-' POINT, AND THE SHIELD TO

THE 'G' POINT.

TC-CAKP		   TWO PIN, MALE, ‘K-TYPE’ THERMOCOUPLE CONNECTOR.

OMEGA CAT. #SMPW-CC-K-M. SCREW TENSION CONNECTIONS,

BEIGE SHELL,COMPENSATING ALLOY IN CONNECTOR IS ‘+’ =

CHROMEGA (YELLOW WIRE)AND ‘-‘ = ALUMEL (RED WIRE).

TC-CCF		TWO PIN FEMALE CONNECTOR, FLAT TERMINALS, SCREW TENSION

CONNECTIONS, COLOR OF SHELL IS BLUE, COMPENSATING ALLOY

USED IN CONNECTOR IS '+' = COPPER, '-' = CONSTANTAN.

OMEGA	CAT. #SMP-T-F.

TC-CCM		TWO PIN MALE CONNECTOR, FLAT TERMINALS, SCREW

TENSION CONNECTIONS, COLOR OF SHELL IS BLUE,

COMPENSATING ALLOY USED IN CONNECTOR IS '+' = COPPER,

'-' = CONSTANTAN. OMEGA CAT. #SMPW-CC-T-M.

TC-CCP		TWO PIN MALE THERMOCOUPLE CONNECTOR, OMEGA CAT.						1PR28CC

#OST-T-M, SCREW TENSION CONNECTIONS, COLOR OF SHELL

BLUE, CONPENSATING ALLOY USED IN CONNECTOR IS '+' =

COPPER,'-' = CONSTANTAN.

TC-CCS		TWO PIN FEMALE THERMOCOUPLE CONNECTOR, OMEGA CAT-# 					1PR28CC

OST-T-F, SCREW TENSION CONNECTIONS, COLOR OF SHELL

BLUE, CONPENSATING ALLOY USED IN CONNECTOR IS '+' =

COPPER, '-' = CONSTANTAN.

TC-JNC		COPPER AND CONSTANTAN CONDUCTORS ARE STRIPPED BACK					1PR28CC

APPROX. ONE INCH AND ELECTRICALLY WELDED TOGETHER ON

THE VERY END TO FORM A THERMOCOUPLE JUNCTION.

COMPLETED TC IS FASTENED INTO PLACE WITH NON-CONDUCTIVE

EPOXY AND WRAPPED WITH GLASS TAPE.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TC-SLV		COPPER AND CONSTANTAN CONDUCTORS ARE STRIPPED BACK					1PR28CC

APPROX. ONE INCH AND WIRE WRAPPED ONTO EXISTING COPPER

CONSTANTAN PIGTAILS ON DISK LOADED WAVEGUIDE. A SOLDER

SLEEVE IS SOLDERED OVER EACH INDIVIDUAL CONDUCTOR AT

THE WIRE WRAP. INSULATE FINISHED CONNECTIONS WITH

SHRINK TUBING.

TCMS04S		   FOUR PIN, FEMALE, ‘K-TYPE’, 350 DEG CELCIUS BAKEABLE,

THERMOCOUPLE CONNECTOR. ISI CONNECTORS P/N: 9923038.

COMPENSATING ALLOY IN CONNECTOR IS ‘+’ = CHROMEL

(YELLOW WIRE) AND ‘-‘ = ALUMEL (RED WIRE).

TC400NMC		COAXIAL CONNECTOR, TYPE N MALE PLUG, KNURLED, TIMES MICROWAVE SYSTEMS.

CAT. #TC-400-NMC											 LMR400,LMR400FR

(BCM TOROID & BLEN)

TC400NMHX		COAXIAL CONNECTOR, TYPE N MALE PLUG, SOLDER, HEX, TIMES MICROWAVE SYSTEMS.

CAT. #TC-400-NMH-X

LMR400,LMR400F

(BCM TOROID & BLEN)

TNC58			COAXIAL CONNECTOR, TNC CABLE PLUG. TIMES EZ-200-TM		RF SYSTEM

P/N 3190-1266 SPRING FIT/CRIMP FOR USE WITH LMR400FR

50 OHM COAX 500 VRMS (MAX) CRIMP TOOL CT-240/200/195/100

3190-667 CRIMP TOOL FOR LMR-100, 195, 200 AND 240 CONNECTORS.

TNC223		COAXIAL CONNECTOR, TNC CABLE PLUG. KINGS CAT. 			OSC FANOUT		RG223

NO. KA-59-45 OR KA-59-87. USE KINGS CRIMPING TOOL

KTH-1000 WITH DIE	KTH-2001 AND TRIM CODE 401.

TCA02ADN	   SEE TERMINAL PLUG CODE DEFINITION AT THE BEGINNING OF

THIS SECTION. MFG: PHOENIX CONTACT, P/N:1881325 ,

DESCRIPTION: COMBICON, FK-MC 0,5/2-ST-2.5 OR EQUIVALENT.

TCA06ADN	   SEE TERMINAL PLUG CODE DEFINITION AT THE BEGINNING OF

THIS SECTION. MFG: PHOENIX CONTACT,P/N:1881367 ,

DESCRIPTION: COMBICON, FK-MC 0,5/6-ST-2.5 OR EQUIVALENT.

TCA12ADN	   SEE TERMINAL PLUG CODE DEFINITION AT THE BEGINNING OF

THIS SECTION. MFG: PHOENIX CONTACT, P/N:1881422 ,

DESCRIPTION: COMBICON,FK-MC 0,5/12-ST-2.5 OR EQUIVALENT.

TCC02AAS		SEE TERMINAL PLUG CODE DEFINITIONS AT THE BEGINNING

OF THIS TERMINATION DESCRIPTION SECTION.

VARIOUS MANUFACTURERS.

TCC03AAN		SEE TERMINAL PLUG CODE DEFINITIONS AT THE BEGINNING

OF THIS TERMINATION DESCRIPTION SECTION.

VARIOUS MANUFACTURERS.

TCC08ABN		SEE TERMINAL PLUG CODE DEFINITIONS AT THE BEGINNING

OF THIS TERMINATION DESCRIPTION SECTION.

MFG: PHOENIX CONTACT, P/N: 1803633, DESCRIPTION: COMBICON,

MC 1.5/8-ST-3.81 OR EQUIVALENT.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TCE08ABN		SEE TERMINAL PLUG CODE DEFINITIONS AT THE BEGINNING

OF THIS TERMINATION DESCRIPTION SECTION.

MFG: PHOENIX CONTACT, P/N: 1757077, DESCRIPTION:

COMBICON, MSTB 2.5/8-ST-5.08 OR EQUIVALENT.

MFG: WEIDMULLER, P/N:1716380000, DESCRIPTION:BL 5.08/08.

TCC10AAS		SEE TERMINAL PLUG CODE DEFINITIONS AT THE BEGINNING

OF THIS TERMINATION DESCRIPTION SECTION.

VARIOUS MANUFACTURERS.

TE2S		   TWO PIN CONNECTOR, FEMALE, CRIMP CONNECTIONS.

TE CONNECTIVITY P/N: 177898-1.

(SEE INFORMATION PAGE 62 )

TE12S		   TWELVE PIN CONNECTOR, FEMALE, CRIMP CONNECTIONS.

TE CONNECTIVITY P/N: 917354-1.

(SEE INFORMATION PAGE 76 )

TT4P			FOUR PIN MALE CONNECTOR, BURNDY TYPE "TRIM-			CHOPPER		2C22MS,1PR22OS,

TRIO", CAT. NO.G6F-10-4-PNE, SLAC S/N59-299-206-01.					7C22OS

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT4PR			FOUR PIN MALE CONNECTOR, BURNDY TYPE "TRIM			CHOPPER,MAG PS	2C22MS,2PR22OS

TRIO", CAT. NO.GOB-10-4-PNE, SLAC S/N59-299-406-01.					1PR20OS,4C20OS

FOR #16-20 WIRE, USE BURNDY CONTACT RM16M-23D28,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE BURNDY CONTACT RM20M-12D28,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE BURNDY CONTACT RM24M-9D28,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT4S			FOUR PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM			CHOPPER,MAG PS	2C22MS,2PR22OS,

TRIO", CAT. NO.,G6F-10-4-SNE, 								1PR20OS,4C20OS

SLAC S/N 59-299-206-02.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT4SR			FOUR PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM

TRIO", CAT. NO.GOB-10-4-SNE, SLAC S/N59-299-406-02.		CHOPPER,MAG PS	2C22MS,2PR22OS,

FOR #16-20 WIRE, USE CONTACT RC16M-23, 							1PR20OS,4C20OS

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT4SW			FOUR PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM			RTD			2PR24IS

TRIO", CAT. NO.G6F-10-4-SWE, (NOTE OFFSET KEYING).

NOT A	SLAC STORES ITEM.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N 59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT8P			EIGHT PIN MALE CONNECTOR, BURNDY TYPE "TRIM-						3PR24IS,4PR18TC,

TRIO", CAT. NO.G6F-12-88-PNE, 								8C18OS

SLAC S/N59-299-206-03.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT8PR			EIGHT PIN MALE CHASSIS-MOUNT CONNECTOR, BURNDY TYPE		LVDT			3PR24IS,4PR22IS

"TRIM-TRIO" CAT. NO. G0B-12-88-PNE,

SLACS/N59-299-406-03.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N 59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT8S			EIGHT PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM			RF SYS		2C22MS,8C18OS,

TRIO",CAT. NO. G6F-12-88-SNE, 								4PR18TC

SLAC S/N59-299-206-04.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT8SR			EIGHT PIN FEMALE CHASSIS-MOUNT CAT. 							4PR18TC

NO. G0F-12-88-SNE, SLAC S/N59-299-406-04.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT12P			TWELVE PIN MALE CONNECTOR, BURNDY TYPE "TRIM-						1PR22OS, 12C16/3V

TRIO", CAT. NO. G6F-14-92-PNE, 								12C18/3V

SLAC S/N59-299-206-05.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT12PR		   TWELVE PIN MALE RECEPTACLE, BURNDY TYPE "TRIM				    12C18OS

TRIO" CAT.NO. GOB1492PNE, SLAC S/N59-299-406-06.

FOR #16-20 WIRE, USE BURNDY CONTACT RC16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1

AND STOP SL-39 ONLY.

FOR #20-22 WIRE, USE BURNDY CONTACT RC20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10

AND STOP SL-40 ONLY.

FOR #24-26 WIRE, USE BURNDY CONTACT RC24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT12S			TWELVE PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM						6PR22OS, 7C18TC,

TRIO", CAT. NO.G6F-14-92-SNE, 								1PR20OS, 12C16/3V

SLAC S/N59-299-206-06.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT12SR		TWELVE PIN FEMALE RECEPTACLE, BURNDY TYPE "TRIM						12C18OS

TRIO" CAT" GOB1492SNE, SLAC S/N59-299-406-05.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT19P			NINETEEN PIN MALE CONNECTOR, BURNDY TYPE "TRIM						1PR22OS,19C18/3V,

TRIO", CAT. NO. G6F-16-19-PNE, 								12C16T3V

SLAC S/N59-299-206-07.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT19PR		NINETEEN PIN MALE RECEPTACLE, BURNDY TYPE "TRIM						12C18OS

TRIO" CAT. NO. GOB1619PNE,SLAC S/N59-299-406-07.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT19S			NINETEEN PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM					12C18OS,11PR22OS,

TRIO", CAT. NO., G6F-16-19-SNE, 								19C16T3V,19C18T3V,

SLAC S/N59-299-206-08.										12C18T3V

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT19SR		NINETEEN PIN FEMALE RECEPTACLE, BURNDY TYPE "TRIM

TRIO" CAT. NO. GOB1619SNE,SLAC S/N59-299-406-08.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT22P			TWENTY-TWO PIN MALE CONNECTOR, BURNDY TYPE "TRIM

TRIO", CAT. NO. G6F-18-22-PNE, SLAC S/N59-299-206-09.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT22S			TWENTY-TWO PIN FEMALE CONNECTOR, BURNDY TYPE

"TRIM TRIO", CAT. NO. G6F-18-22-SNE, SLAC

S/N59-299-206-10.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT30P			THIRTY PIN MALE CONNECTOR, BURNDY TYPE "TRIM

TRIO", CAT. NO. G6F-20-30-PNE,

SLAC S/N59-299-801-11.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N 59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT30S			THIRTY PIN FEMALE CONNECTOR, BURNDY TYPE "TRIM						15PR22OS

TRIO", CAT. NO. G6F-20-30-SNE,

SLAC S/N59-299-206-12.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TT38P			THIRTY-EIGHT PIN MALE CONNECTOR, BURNDY TYPE "TRIM

TRIO", CAT. NO., G6F-22-38-PNE,

SLAC S/N 59-299-206-13.

FOR #16-20 WIRE, USE CONTACT RM16M-23,

SLAC S/N59-299-801-07.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RM20M-12,

SLAC S/N59-299-801-05.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RM24M-9,

SLAC S/N59-299-801-12.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TT38S			THIRTY-EIGHT PIN FEMALE CONNECTOR, BURNDY TYPE

"TRIM TRIO", CAT. NO. G6F-22-38-SNE,

SLAC S/N59-299-206-14.

FOR #16-20 WIRE, USE CONTACT RC16M-23,

SLAC S/N 59-299-801-08.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S3-1 AND

STOP SL-39 ONLY.

FOR #20-22 WIRE, USE CONTACT RC20M-12,

SLAC S/N59-299-801-06.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-10 AND

STOP SL-40 ONLY.

FOR #24-26 WIRE, USE CONTACT RC24M-9,

SLAC S/N59-299-801-11.

USE HAND CRIMPING TOOL M10S-1 WITH DIE S-9 AND

STOP SL-40 ONLY.

TX22			TWINAX CONNECTOR, CABLE PLUG. KINGS CAT. 				INJECTION 		RG22

NO. KU-59-18, SLAC S/N. 59-299-026-01. USE KINGS 		TOROIDS

CRIMPING TOOL KTH-1000 WITH DIE KTH-2004 AND TRIM

CODE 601. INSURE PIN-# TO PIN-# CONTINUITY.

TX227241		TWINAX CONNECTOR, CABLE PLUG, 2 CONDUCTOR, 						TWC9207N

TYCO CAT# 227241-1.

TX108			TWINAX CONNECTOR, CABLE PLUG, 2 CONDUCTOR, POMONA		SDR PULSE		RG108A

CAT #4957									KICKER		BELDEN 9272

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

TXBJ22		TWINAX CONNECTOR, BULKHEAD JACK, KINGS 				FFTB BCS		RG22

CAT. #KU-19-06, SLAC S/N59-299-026-02. USE KINGS

CRIMPING TOOL KTH-1000 WITH DIE. KTH-2004 AND TRIM

CODE 601. INSURE PIN-# TO PIN-# CONTINUITY.

UNIQ-Y		SLAC MADE POWER CABLE TO FEED AN UNIQ UP 900-CL CAMERA

AND A EDT RCX CAMERALINK TO FIBER CONVERTER.

DETAILS FOR THE UNIQ-Y CONNECTIONS ARE SHOWN

IN DRAWING CA-261-801-30.

USER			SPECIAL EXPERIMENTAL ONLY CONNECTOR, USER TO 						MISC

TERMINATE AND CONNECT. MAY BE OF VARIOUS MISC.

SPECIAL TYPES. THIS DESIGNATION IS NEVER TO BE USED

FOR OPERATIONAL FACILITY MAINTAINED SYSTEMS.

USBAP			CONNECTOR, 4 PIN, USB TYPE-A, PLUG, WIRE RANGE 20-28 AWG,

KYCON P/N: KUSBX-AP-KIT-SC. NO INSULATION BOOT.

USBBP			CONNECTOR, 4 PIN, USB TYPE-B, PLUG, WIRE RANGE 20-28 AWG,

KYCON P/N: KUSBX-BP-KIT-SC.NO INSULATION BOOT.

UVC90			NINETY PIN MALE CONNECTOR. THIS CONNECTOR IS SUPPLIED		CID HV CNTLR.	18PR22OS

WITH UNIT. MFR. UNIVERSAL VOLTRONICS CORP.

VAT3S			CONNECTOR, FEMALE, 3 PIN CABLE RECEPTACLE,

VAT P/N N-E506-007. CONTACT/ORDER INFORMATION: VAT AG,

(925) 944-3570. CABLE ASSEMBLY PART NUMBER: 770CS-99L(X)

(X IS LENGTH IN METERS). THE CONNECTOR(S) WILL BE

SUPPLIED BY THE VENDOR ALREADY ATTACHED TO THE CABLE.

VAT7S			SEVEN PIN CONNECTOR SUPPLIED WITH ISOLATION VALVE. 		VAC.VALVES		5PR20OS,9C18J

IRMA FRANZ BINDER P/N 696-299-0234-00-07, ORDER FROM

VAT, WIRE IN SEQUENCE USING COLOR CODE 1R ONLY, CUT

OFF UNUSED WIRES.

VAT12P		CONNECTOR, MALE, 12 PIN CABLE PLUG, VAT P/N 81173-R1.

CONTACT/ORDER INFORMATION: VAT AG, (925) 944-3570.

CABLE ASSEMBLY PART NUMBER: 770CV-89L(X) (X IS LENGTH IN

METERS).THE CONNECTOR(S) WILL BE SUPPLIED BY THE VENDOR

ALREADY ATTACHED TO THE CABLE.

VAT12S		CONNECTOR, FEMALE, 12 PIN CABLE RECEPTACLE, VAT

P/N 81167-R1, SOCKET CONTACTS P/N RC16M23K, INTERNET

ADDRESS WWW.VAT DR. #125-902, FAST SHUTTER SYSTEM.

TERM			TERMINATION DESCRIPTION							APPLICATION		USED ON CABLE TYPE

VGAUGE		SPECIAL PREWIRED ION-GAUGE CONNECTOR.							IG-CABLE

VG-CON		SPECIAL PREWIRED FOUR PIN (IG22) AND BNC							IG-CABLE

CONNECTORS FOR CONNECTION OF AN ION-GAUGE TO A VACUUM

GAUGE LONG-LINE ADAPTOR DROP-BOX.

VIK-44		FORTY-FOUR PIN CONNECTOR, PCB EDGEON TYPE, VIKING P/N					19PR22IS

2VH22/1AN5, SLAC S/N59-299-302-02. USE VIKING HOOD P/N

036-0121-002, SLAC S/N 93-299-300-02. SOLDER CONNECTIONS.

WNB			WIRE NUT, BLUE, SIZE 12-6, WITH INNER CONDUCTING

TAPERED SPRING.

WNG			WIRE NUT, GRAY, SIZE 14-8, WITH INNER CONDUCTING

TAPERED SPRING.

WNR			WIRE NUT, RED, SIZE 16-10, WITH INNER CONDUCTING

TAPERED SPRING.

WNY			WIRE-NUT, YELLOW, SIZE 12-18, WITH INNER CONDUCTING		MISC.

TAPERED SPRING.

W1			COPPER/CONSTANTAN WIRE PAIRS. STRIP THE INSULATION 		RF CAVITY		10PRTHRM, 1PR28CC

AND PUT THE COPPER CONDUCTOR (BLUE INSULATION) OF 		THERMOCOUPLES

THE FIRST PAIR UNDER THE '+' SCREW OF THE INDICATED

STARTING CHANNEL, AND THE CONSTANTAN CONDUCTOR

(RED INSULATION) UNDER THE '-' SCREW. CONTINUE

CONNECTING THE THERMOCOUPLE PAIRS IN THE SAME MANNER,

UP THROUGH THE LAST INDICATED PAIR AND/OR CHANNEL.

XLR3P			MALE THREE PIN AUDIO CONNECTOR, CANNON XLR-3-12C,					1PR16AS, 1PR16T3V

SLAC S/N59-299-415-07. SOLDER CONNECTIONS.

XLR3S			FEMALE THREE PIN AUDIO CONNECTOR, CANNON AXR-3-11R,					1PR16T3V

SLAC S/N59-299-415-03. SOLDER CONNECTIONS.

### Table 4 - Trim Codes for Coaxial Cable Terminations

CROSS-REFERENCED LIST OF COAXIAL CABLE TERMINATION PROCEDURES

ALTERNATE            CRIMPING                      JACKET                 DIELECTRIC

TERM         CABLE       CONNECTOR            TOOL DIE     TRIM           TRIM JIG                  TRIM JIG

NO.          TYPE        PART #'S.             NO.         CODE         KINGS       PEP*        KINGS       PEP**

N11          RG11         KN-59-67            KTH-2003    402M        KTJ-60      KTJ-60P     KTD-28      KTD-28P

KN-59-132

KN-59-201           KTH-2004    480         KTJ-137     KTJ-60P     KTD-138     KTD-138P

KN-59-202

TX22         RG22         KU-59-18            KTH-2004    601         23          ---         ---         ---

BNC58        RG58         KC-59-290           KTH-2001    401         KTJ-57      KTJ-57P     KTD-25      KTD-25P

KC-59-291

HV58         RG58         KINGS 1065-1        KTH-2001    474         KTJ-86      KTJ-57P     KTD-128     ---

KINGS 1065-2        KTH-2001$   419         KTJ-71      KTJ-57P     KTD-68      KTD-68P

SHV58        RG58R        KINGS 1705-2        KTH-2061    441         KTJ-72      KTJ-57P     KTD-136     KTD-136P

TNC58        RG58         KA-59-44            KTH-2001    401         KTJ-57      KTJ-57P     KTD-25      KTD-25P

KA-59-103

HV-C         LASL C       KINGS 1065-2        KTH-2001    419         KTJ-71      KTJ-57P     KTD-68      KTD-68P

REYNOLDS 167-3554   KTH-2001$   REY1        ---         KTJ-57P     ---         ---

BNC59        RG59         KC-59-293           KTH-2002A   401         KTJ-57      KTJ-57P     KTD-26      KTD-26P

KC-59-294

SHV59J       RG59R        KINGS 1702-1        KTH-2062    441         KTJ-72      KTJ-57P     KTD-134

SHV59P       RG59R        KINGS 1705-1       KTH-2062     418         KTJ-72      KTJ-57P     KTD-136      KTD-136P

BNC62        RG62         KC-59-293          KTH2002A     401         KTJ-57      KTJ-57P     KTD-26       KTD-26P

KC-59-294

N213         RG213       KN-59-67           KTH-2003     402M        KTJ-60      KTJ-60P     KTD-28       KTD-28P

KN-59-132

KN-59-201          KTH-2004     480         KTJ-137     KTJ-60P     KTD-138      KTD-138P

KN-59-202

HV213        RG213R      KINGS 1765-1       KTH-2078     475         KTJ-124     ---         KTD-179      ---

REYNOLDS 167-3516  KTH-2003$    REY2        ---         KTJ-60P     ---          KTD-REY2

N214         RG214       KN-59-68           KTH-2004     402M        KTJ-60      KTJ-60P     KTD-28       KTD-28P

KN-59-104

KN-59-105

BNC223       RG223       KC-59-80           KTH-2001     401         KTJ-57      KTJ-57P     KTD-25       KTD-25P

KC-59-162

TNC223       RG223       KA-59-45           KTH-2001     401         KTJ-57      KTJ-57P     KTD-25       KTD-25P

KA-59-87

$ THE CENTER CONDUCTOR PIN MUST BE SOLDERED, NOT CRIMPED. * AND ** SEE NOTES UNDER TRIM CODE CHART ON NEXT PAGE.

CROSS-REFERENCED LIST OF COAXIAL CABLE TERMINATION PROCEDURES (continued)

TRIM CODE CHART

SEE KINGS 'K-GRIP'CATALOG FOR DETAILS OF 'A', 'B', 'C' AND 'D' DIMENSIONS.

PEP *		 PEP **

JACKET	 DIELECTRIC

CODE         A + B          A            B            C            D           TRIM JIG   TRIM JIG

209A         13/16" (0.81)  19/32"       7/32"        (0.43")      5/32"

401          37/64"         23/64"       7/32"        15/32"       7/64"        KTJ-57P     KTD-25P,26P

(0.58")                                  (0.47")

402M         19/32"         5/16"        9/32"        3/8"         7/32"        KTJ-60P     KTD-28P

(0.59")                                  (0.38")

415M         1 5/32"        15/32"       7/32"        17/32"       5/32"        KTJ-65      KTD-38

(1.16")                                  (0.53")

418          59/64"         45/64"       7/32"        13/16"       7/64"        KTJ-57P     KTD-136P

(0.92")                                  (0.80")

419          1 3/32"        7/8"         7/32"        63/64"       7/64"        KTJ-57P     KTD-68P

(1.09")                                  (0.98")

432          31/64"         17/64"       7/32"        (0.39")      3/32"        KTJ-78      KTD-116

(0.48")

441          15/16"         23/32"       7/32"        49/64"       5/32"        KTJ-57P     KTD-136P

(0.94")                                  (0.77")

465          19/32"         1/4"         11/32"       7/16"        5/32"        KTJ-        KTD-

(0.59")                                  (0.43")

474          1 1/8"         29/32"       7/32"        57/64"       15/64"       KTJ-57P     KTD-128P

(1.13")                                  (0.89")

475          1 15/16"       1 23/32"     7/32"        1 5/8"       5/16"        KTJ-124     KTD-179

(1.94")                                  (1.63")

480          11/16"         9/32"        13/32"       1/2"         3/16"        KTJ-60P     KTD-138P

(0.69")                                  (0.50")

601          2 1/4"         2"           1/4"         1/16"        5/32"        KTJ-23      ---          E: 5/32"

(2.25")                                  (0.06")

REY1         1  3/16"       0.76"        0.43"        1" (1.00")   3/16"        ---         ---

(1.19")

REY2         1 13/16"       1 23/64"     29/64"       (1.54")      17/64"       KTJ-REY2    KTD-REY2

(1.81")

* THE TYPES WITH A "P" SUFFIX ARE MODIFIED

KINGS JIGS THAT REDUCE THE NUMBER OF DIFFERENT

TYPES OF JIGS NEEDED. THESE JIGS HAVE EXTRA SLOTS

FOR DIFFERENT BLADE SPACINGS AND A HOLE IN THE END,

SO THAT THE DIELECTRIC AND THE CENTER CONDUCTOR

CAN BE LEFT LONG FOR TRIMMING WITH THE DIELECTRIC

TRIM JIG.

** THE TYPES WITH A "P" SUFFIX ARE MODIFIED

KINGS JIGS THAT DUE TO THE MODIFICATION ALLOW

TRIMMING OF THE CENTER CONDUCTOR AND MAKE THE

CUTTING OF THE CABLE DIELECTRIC EASIER AND

CLEANER.

### Table 5 - Revision notes for this document.

a. 85-01-25: Original issue for review and bid package (preliminary,rev X).

b. 85-01-31: Second issue (still preliminary, rev. X)

1. The TERMINATION codes in Section 2 were changed from alpha

to numeric characters, to avoid confusion with the subcontractor action

codes.

2. Some minor editing and spelling changes were also made at this time.

3. Some connector and cable descriptions have been added.

c. 85-05-29: Third issue (still preliminary, rev. X)

1. Additional editing has been done, additional descriptions added.

2. Some crimp tooling additions and corrections were made.

d. 85-06-07: First formal (-R0) release.

e. 86-03-05: Second formal (-R1) release.

1. Added 'KAnn' and 'KMnn' to Cable Installation Schedule Format Description

under 'ORIGIN / LOCATION'.

2. Added 'PINK' and 'TAN' to Table 1.

Added additional wire color code tables: 1L, 1M, 1N, 1P, 1Q, 1R, 1S, 1T and 1U.

Corrected color code in Table 1R.

3. Added MCM series definitions, and single wire estimating diameters to the beginning

of Table 2.

Corrected the SLAC S/N for MS6PSB (from -01 (error), to -51).

Changed the description for 2C16OS to show the same as 1PR16OS.

Corrected the O.D and Belden Cat No. for 2PR22OS.

Changed the description for 4PR16OS to include additional details.

Corrected the O.D. and added Alpha Cat. No. to 8C16/3V.

Corrected the voltage rating for 8C18OS.

Added Alpha No. and Color Code to 8PR16TS.

Corrected the O.D. and Belden Cat. No. for 18PR22OS.

Added additional termination information to 18PR22OS.

Added 'OVERALL SHIELD' to description for 27C20OS.

Added 'TRAY CABLE' to description for 27PR22OS.

Changed description for 50C16TC to show the same as 50C16/3V.

Added description to HVSPEC1.

Corrected Color Code on 6PR24IS.

Corrected Slac No. and MFG. on 18PR22OS.

Added additional cable types to Table 2: 1/2HELGF, #2-FLEX,

1PR16AS, 1PR20OS, 1PR28CC, 2C8TYR, 2C10TYR, 2C12TYR, 2C14TYR,

2C16/3V, 2C16OS, 2C16T6V, 2C18TC, 2C20OS, 2PR20IS, 2PR22OS, 3C16/3V,

3C16FLX, 3C16TYR, 3C20/3V, 3PR22OS, 4C8SHLD, 4C8TYR, 4C10TYR,

4C12OJ, 4C16TYR, 4C12TYR, 4C16FLX, 4C16OS, 4PR16IS, 4PR16TC, 4PR18TC,

5C16/6V, 5C18TC, 5PR20OS, 6C16OS, 6C18TC, 6PR22OS, 6PR24IS, 7C18TC,

8C12T6V, 8C16/3V, 8C18OS, 8PR16OS, 8PR20IS, 11PR22OS, 12C10TYR,

12C12/3V, 12C16/6V, 12C12TYR, 12C18OS, 12C18TC, 12PR16AS, 12PR22OS,

15PR22OS, 15PR22TS, 18PR22OS, 19C12/6V, 19C16/3V, 24PR16TC, 26C16/3V,

27C20OS, 50C16/3V, 50C16TC, BRBW12, HVSPEC1, IG-CABLE, RG59B

4. Added additional termination types to Table 3: ACJBX, ACP,

ACP15, ACP20, ACR, AMP24P, AMP36P, BP(-ccc), BP-01, BP-02,

CED-30, D37F, D37F-A, D37M, D37M-A, DAY-20, FIXED, GP-CON,

GP-GAU, HN214, HR13P, HR13S, HV214, IG-CP6, IPVB, the 'LB' series,

LB1-6, LB4-6, LB35-8A, LB6-3, LB6-3A, LEMO-A, LFB-E, LFR-H, LFR-J,

LFR-K, LRB-A, LRB-B, LRB#6, LRB#8, LRB#10, LRR1/4, LRR#6, LRR-A,

LR6#10, LR8-6, LR8U10, LSB#10, LSR-D, LSR-E, LSR#8, LSR#10, MS-HVS,

MS5P, MS6F, MS6M, MS6PR, MS8PA, MS8PAR, MS8PW, MS8PY, MS8SA, MS10SA,

MS11PR, MS21SW, MS26PA, MS26PG, MS26SA, MS32P, N1/2HG, N223, PP50G,

PP100G, PS50/2, RS50G, RS100G, RTDS, SOLDER, STRIP, TC-CCP, TC-CCS,

TC-JNC, TC-SLV, TCSCCP, TCSCCS, TT4P-1, TT4P-2, TT4SW, TT8F, TT8M,

TT8P, TT8PR, TT8S-A, TT12P, TT12P1, TT12S, TT19P, TT19S, TT19S1,

TT22P, TT22S, TT30P, TT30S, TT38P, TT38S, VGAUGE, VG-CON, VAT7S,

XLR3P and XLR3S.

Added model no. to HV220.

Added tool '69062' to terminations LR8#10 and LB8-2.

Changed crimping tool '69062' to '59975-1' for terminations LB4-6, LR6#10, LR8#10,

and LB8-2.

Changed 'Kings Cat. No. 1765-2' to 'Kings Cat. No. 1765-1', and added 'OR DIE KTH-1078' to

termination HV213.

Changed many termination descriptions: from, the reference to a specific color code: to, a

reference to the wire type for the color code.

Corrected the description for LFB-D to remove the erroneous call-out for 'no connection'

to point 48.

Corrected the description for LFY-B to include wiring for color code 1B.

Corrected the SLAC P/N for SHV59J.

Changed LR4-3/8 to LB4-6.

Changed LR8-1/4 to LB8-2.

Added crimping, tooling and trim codes to SMA223 and SMR223.

5. Added Trim Code 432.

f. 87-01-15: Third Formal (-R2) Release.

1. Added additional wire color code tables: 1V.

Added additonal cable types to Table 2: 1/4"HEL, 3/8"HEL, 3C14FLX, 5C16T6V,

12C20J and 19C16/6V.

2. Added additional termination types to Table 3: AMP48P, LEMO, N1/4HP and N3/8HP.

Corrected and expanded the descriptions for D37F and D37M.

g. : WORKING VERSION (RX2) NOT RELEASED.

1. Added additional wire color code tables: 1W

Added additonal cable types to Table 2: 7C22OS.

2. Added additional termination types to Table 3: TT4P

Added additional termination types: DAY-50 & MS3S-S.

3. Added addition cable type to Table 1P: 12PR22OS.

4. Added O.D and Belden Cat. #8312 to 12PR22OS.

5. Added additional cable types to Table 2: 25PR24IS, 51PR220S, RG11A, RG108A.

Added additional termination types to Table 3: D50F, TT12S,LFR-L, USER.

Corrected RG11 to RG11TRI.

Added additional wire color code table: 1X

6. Added additional cable types to Table 2: 4PR24IS, 12C18/3V